## Sheet1
DATE OF OPENING 08.08.2016
PRICE SCHEDULE -P-1
Sl. No. | Item Description | Qty | Units | Estimated Rate | Ex-Works Prices to be entered by the Bidder (in. Rs.) | Total Amount of Ex-Works Prices (in. Rs.) (5x3) | Freight & Insurance Charges to be entered by the Bidder (in Rs.) | Total Amount of Freight & Insurance Charges (in Rs.) (7x3) | Unit Erection Charges incl. Service Tax (in Rs.) | Total Amount of Erection Charges incl. Service Tax (in Rs.) (9x3) | Total Unit prices incl. Supply, F&I, Erection & all Taxes (In Rs.) (5+7+9+12) | Taxes & Duties per unit (in Rs.) | Total Value of Taxes & Duties (in Rs.) (12x3) | Total Amount incl. Supply, F&I, Erection & all Taxes (in Rs.) (11x3)* | Bought out or Direct Items to be specified by the Bidder
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
1 | Supply & Erection of LT Aluminium armoured XLPE Single Core Cable of size for shaperate from different transformers to the distribution boxes/ panels / other arrangements as per site conditions of 1x630 Sq.mm. | 0.64 | Km. | NTQ | NTQ | NTQ | NTQ | NTQ
2 | Supply & Erection of LT Aluminium armoured XLPE Single Core Cable of size for shaperate from different transformers to the distribution boxes/ panels / other arrangements as per site conditions of 1x400 Sq.mm. | 2.24 | Km. | NTQ | NTQ | NTQ | NTQ | NTQ
3 | Supply & Erection of LT Aluminium armoured XLPE Single Core Cable of size for shaperate from different transformers to the distribution boxes/ panels / other arrangements as per site conditions of 1x240 Sq.mm. | 4 | Km. | NTQ | NTQ | NTQ | NTQ | NTQ
4 | Supply & Erection of LT Aluminium armoured XLPE Single Core Cable of size for shaperate from different transformers to the distribution boxes/ panels / other arrangements as per site conditions of 1x120 Sq.mm. | 5.12 | Km. | NTQ | NTQ | NTQ | NTQ | NTQ
5 | Al. crimping lugs (630/400/240/120/70/50) sq.mm. | 2048 | Nos.
6 | Supply & Erection of 1100 V Grade, PVC sheathed steel strip armoured, aluminum conductor LT XLPE insulated cable for sizes of 3.5Cx400 sq.mmXLPE | 21 | Km. | NTQ | NTQ | NTQ | NTQ | NTQ
7 | Supply & Erection of 1100 V Grade, PVC sheathed steel strip armoured, aluminum conductor LT XLPE insulated cable for sizes of 3.5Cx240 sq.mmXLPE | 18 | Km. | NTQ | NTQ | NTQ | NTQ | NTQ
8 | Supply & Erection of 1100 V Grade, PVC sheathed steel strip armoured, aluminum conductor LT XLPE insulated cable for sizes of 3.5Cx120 sq.mmXLPE | 38 | Km. | NTQ | NTQ | NTQ | NTQ | NTQ
9 | Supply & Erection of 1100 V Grade, PVC sheathed steel strip armoured, aluminum conductor LT XLPE insulated cable for sizes of 4x50 sq.mmXLPE | 32 | Km. | NTQ | NTQ | NTQ | NTQ | NTQ
10 | Cable end termination using total double compression brass glands and crimping type Aluminium Thimbles of 3.5CX400sq.mm | 3026 | Nos.
11 | Cable end termination using total double compression brass glands and crimping type Aluminium Thimbles of 3.5CX240sq.mm | 7816 | Nos.
12 | Cable end termination using total double compression brass glands and crimping type Aluminium Thimbles of 3.5CX120sq.mm | 2976 | Nos.
13 | Cable end termination using total double compression brass glands and crimping type Aluminium Thimbles of 4X50sq.mm | 818 | Nos.
14 | Laying, testing & commissioning of sizes of 1100 V Grade, PVC sheathed steel strip armoured, aluminum conductor LT XLPE insulated cable to be laid underground in HDPE pipe of 3.5Cx400 sq.mmXLPE | 3.5 | Km.
15 | Laying, testing & commissioning of sizes of 1100 V Grade, PVC sheathed steel strip armoured, aluminum conductor LT XLPE insulated cable to be laid underground in HDPE pipe of 3.5Cx240 sq.mmXLPE | 6 | Km.
16 | Laying, testing & commissioning of sizes of 1100 V Grade, PVC sheathed steel strip armoured, aluminum conductor LT XLPE insulated cable to be laid underground in HDPE pipe of 3.5Cx120 sq.mmXLPE | 4.98 | Km.
17 | Laying, testing & commissioning of sizes of 1100 V Grade, PVC sheathed steel strip armoured, aluminum conductor LT XLPE insulated cable to be laid underground in HDPE pipe of 4x50 sq.mmXLPE | 2.76 | Km.
18 | Digging of Trench by excavation of earth, laying of bricks to cover the cable and filling of sand & earth ramming and dressing properly with complete job for laying of 1100 V Grade, PVC sheathed steel strip armoured, aluminum conductor LT XLPE insulated cables (for laying of cable as per details writen in the scope of works in the bidd documents). | 81.34 | Running Km.
19 | Back fillng & restoring the road to make it as original including supply of all material. | 81.34 | Running Km.
20 | Supply & laying of HDPE pipe of size by Horizontal drilling for underground piping (trenchless) for above cable at road crossings. Min Depth of pipe shall be 1.2 M below surface of 160 mm dia | 5.14 | Km.
21 | Supply & laying of HDPE pipe of size by Horizontal drilling for underground piping (trenchless) for above cable at road crossings. Min Depth of pipe shall be 1.2 M below surface of 110 mm dia | 4.27 | Km.
22 | Supply & laying of HDPE pipe of size by Horizontal drilling for underground piping (trenchless) for above cable at road crossings. Min Depth of pipe shall be 1.2 M below surface of 50 mm dia | 3.92 | Km.
23 | Supply and marking of manhole 750x600 mm with manhole cover for pulling LT cable in lanes by lanes | 342 | Nos.
24 | Supply , installation and testing of 7x20 SWG GSS Wire for earthing along cables. | 8214 | Kg.
25 | Supply and laying of pipe for small cable to houses of Gl Pipe of 50 mm dia (external area) | 25.2 | Km.
26 | Supply and laying of pipe for small cable to houses of PVC pipe heavy gauge 50 mm dia (underground area) | 65.8 | Km.
27 | Supply and installation of RCC pipe of folloing size of 300 mm | 12 | Km.
28 | Installation of material for Street lighting of Supply and laying (in GI Pipe) of 1100 V Grade, PVC sheathed steel strip armoured, aluminum conductor LT XLPE insulated cable of size 2x10 sq.mm. XLPE (For Street light) | 35 | Km.
29 | Installation of material for Street lighting of Supply and laying (in GI Pipe) of 1100 V Grade, PVC sheathed steel strip armoured, aluminum conductor LT XLPE insulated cable of Gl Pipe of 40 mm dia. Underground | 18 | Km.
30 | Installation of material for Street lighting of Supply & installation of Junction Box on STP/PCC Poles with 900 mm long GI Pipe 25 mm dia. With clamps for street light connection. | 1996 | Nos.
31 | Dismantling of Existing LT overhead line and Transportation of dismantled material to nearest Store.(leaving the poles for street light) | 35 | Ckt. Km.
32 | Supply of Outdoor type LT Disribution Boards with a rupturing capacity of 50KA at 415V or as called for individual items (CPRI Approved manufacturer), openable in front and back suitable for 3 plase, 4 wire, 50Hz AC supply and an ambient temperature of 45 deg. C. The Cubicle should be weather proof, dust proof, vermin Proof and enclosure protection shall be IP-55 as per IS 2147-1962 and IS: 8623. The panels/switches boards shall be fabricated out of 14-SWG CRCA sheet steel and provided with 16 SWG hinged doors including suitable foundation. MAIN LT PANEL AT SUB STATION- 1000 & 630 KVA (Type A-1) Incomer- 1 No. 1250 Amp. TP MDO ACB with Inbuilt MPR Release with On/Off Indicating Light Metering on Incomer - 1 Set of Digital Ammeter with ASS - 1 Set of Digital Voltmeter with VSS - 1 Set of LED type Phase Indicating Light (22.5 mm.) with Control MCBs Outgoing - 7 Set of 400 Amp. TP MCCB with Spreader & Extended handle - 2 Set of 100 Amp. TP MCCB with Spreader & Extended handle | 8 | Nos.
33 | Supply of Outdoor type LT Disribution Boards with a rupturing capacity of 50KA at 415V or as called for individual items (CPRI Approved manufacturer), openable in front and back suitable for 3 plase, 4 wire, 50Hz AC supply and an ambient temperature of 45 deg. C. The Cubicle should be weather proof, dust proof, vermin Proof and enclosure protection shall be IP-55 as per IS 2147-1962 and IS: 8623. The panels/switches boards shall be fabricated out of 14-SWG CRCA sheet steel and provided with 16 SWG hinged doors including suitable foundation. MAIN LT PANEL AT SUB STATION- 400 KVA (Type A-2) Incomer- 1 Set of 800 Amp. TP MCCB with Spreader & Extended handle Metering on Incomer - 1 Set of Digital Ammeter with ASS - 1 Set of Digital Voltmeter with VSS - 1 Set of LED type Phase Indicating Light (22.5 mm.) with Control MCBs Outgoing- 6 Set of 250 Amp. TP MCCB with Spreader & Extended handle ( 5 Nos. + 1 No. for capacitor panel) - 2 Set of 100 Amp. TP MCCB with Spreader & Extended handle | 28 | Nos.
34 | Supply of Outdoor typeLT Disribution Boards with a rupturing capacity of 50KA at 415V or as called for individual items (CPRI Approved manufacturer), openable in front and back suitable for 3 plase, 4 wire, 50Hz AC supply and an ambient temperature of 45 deg. C. The Cubicle should be weather proof, dust proof, vermin Proof and enclosure protection shall be IP-55 as per IS 2147-1962 and IS: 8623. The panels/switches boards shall be fabricated out of 14-SWG CRCA sheet steel and provided with 16 SWG hinged doors including suitable foundation. MAIN LT PANEL AT SUB STATION- 250 KVA (Type A-3) Incomer- 1 Set of 630 Amp. TP MCCB with Spreader & Extended handle Metering on Incomer - 1 Set of Digital Ammeter with ASS - 1 Set of Digital Voltmeter with VSS - 1 Set of LED type Phase Indicating Light (22.5 mm.) with Control MCBs Outgoing- 5 Set of 250 Amp. TP MCCB with Spreader & Extended handle ( 4 Nos. + 1 No. for capacitor panel) - 2 Set of 100 Amp. TP MCCB with Spreader & Extended handle | 75 | Nos.
35 | Supply of Outdoor type LT Disribution Boards with a rupturing capacity of 50KA at 415V or as called for individual items (CPRI Approved manufacturer), openable in front and back suitable for 3 plase, 4 wire, 50Hz AC supply and an ambient temperature of 45 deg. C. The Cubicle should be weather proof, dust proof, vermin Proof and enclosure protection shall be IP-55 as per IS 2147-1962 and IS: 8623. The panels/switches boards shall be fabricated out of 14-SWG CRCA sheet steel and provided with 16 SWG hinged doors including suitable foundation. MAIN LT PANEL AT SUB STATION- 160 KVA (Type A-4) Incomer- 1 Set of 400 Amp. TP MCCB with Spreader & Extended handle Metering on Incomer - 1 Set of Digital Ammeter with ASS - 1 Set of Digital Voltmeter with VSS - 1 Set of LED type Phase Indicating Light (22.5 mm.) with Control MCBs Outgoing- 4 Set of 250 Amp. TP MCCB with Spreader & Extended handle ( 3 Nos. + 1 No. for capacitor panel) - 2 Set of 100 Amp. TP MCCB with Spreader & Extended handle | 96 | Nos.
36 | Supply , installation, testing & commissioning of outdoor type feeder pillar panel to be made of 2 mm CRCA sheet and covers will be 1.6mm CRCA sheet duly powder coated paint including suitable foundation with 400 amps Al. busbar. (Type-B1) Incomer - 250 Amp. TP MCCB - 1 No. Outgoing - 63 Amp. TP MCCB - 6 Nos. | 106 | Nos.
37 | Supply , installation, testing & commissioning of outdoor type feeder pillar panel to be made of 2 mm CRCA sheet and covers will be 1.6mm CRCA sheet duly powder coated paint including suitable foundation with 300 amps Al. busbar. (Type-B2) Incomer - 250 Amp. TP MCCB - 1 No. Outgoing - 63 Amp. TP MCCB - 5 Nos | 75 | Nos.
38 | Supply , installation, testing & commissioning of outdoor type feeder pillar panel to be made of 2 mm CRCA sheet and covers will be 1.6mm CRCA sheet duly powder coated paint including suitable foundation with 300 amps Al. busbar. (Type-B3) Incomer - 100 Amp. TP MCCB - 1 No. Outgoing - 63 Amp. TP MCCB - 4 Nos. | 62 | Nos.
39 | Supply , installation, testing & commissioning of Lockable distribution boxes of size 450X400mm including suitable foundation with bus bar 100 Amp. TPN to feed upto 10 houses (Type C) | 1592 | Nos.
40 | For Street Light Metering of Automation ON/OFF Circuit Breaker Switch | 242 | Nos.
41 | For Street Light Metering of Electronic Meter 1 Phase 20-80 amp with SMC Meter Box | 242 | Nos.
42 | For Street Light Metering of Extra Cost for Cable 16 sq.mm. and installation of above | 242 | Job
43 | PVC Insulated Armoured Consumer Service Cable 2x4 Sq. mm | 12 | Km.
44 | PVC Insulated Armoured Consumer Service Cable 4x6 Sq. mm | 7 | Km.
45 | PVC Insulated Armoured Consumer Service Cable 4x10 Sq. mm | 6 | Km.
46 | PVC Insulated Armoured Consumer Service Cable 4x16 Sq. mm | 6 | Km.
egRoiw.kZ uksV%&¼1½ izfrHkkxh QekZsa ds izkIr njksa dk vkdyu ldy laxf.kr nj ¼lkexzh rFkk dk;kZsa ds lkFk½ ds vk/kkj ij fd;k tk;sxkA
¼2½ NTQ ds LFkku ij njsa ugha Hkjh tk;ssaxhA