## BIRNO
APPROXIMATE BILL OF QUANTITY FOR M&R OF MISC. CIVIL WORKS
AT 33/ 11 K.V. BIRNO, GHAZIPUR
Sl. | ITEM OF WORKS | UNIT | QUANTITY | RATE | AMOUNT
1 | 2 | 3 | 4 | 5 | 6
1 | Dismantiling of existing damaged Mud Faska over the roof. Cleaning the surface with wire brush, removal and disposal of rubbish at a distance 100 meters also including the cost of celaning and stacking of usable materials etc. including all labour, material required for porper completion of work.(CSI No. 15.14) | Sqm | 102.64 | 107 | 10982.48
2 | Dismantling brick work or stone work in lime or cement mortar and including stacking of materials as directied by the E/I. within a distance of 60 metres. (CSI.No.15.01) | Cum. | 2.89 | 389 | 1124.21
3 | Providing of Dr. fixit 301 pidicrete URP & mixing it properly with cement in the proportion of 1:1.5 apply two coat to the prepared surface including cost of labour, material T&P etc. as required for proper completion of work as directed by E/I.(NSI) | Sqm | 102.64 | 262 | 26891.68
4 | R.C.C. work with cement, approved coarse sand and 2 cm. (3/4") gauge approved stone ballast in the proportion of 1:1.5:3 in the SLABS excluding reinforcement and its bending but including its fixing and binding the same with 24 BWG, G.I. binding wire and including necessary centering and shuttering etc. and also including supply of all materials, labour and T&P etc. required for proper completion of the work. (Binding wire to be supplied by the contractor free of cost).(C.S.I. No. 5.24) | Cum. | 10.8 | 9117 | 98463.6
5 | Mild steel of or iron in plain work such as reinforced concrete or reinforced brick work. (when not included in over all rates) wrought to required shape as necessary including bending for proper completion of the work and including supply of steel, its wastage, bend hooks, and authorized overlapping shall be measured. Rainforcement steel of tensile strength 415 N/MM² steel, TMT steel rods of TATA/ SAIL/KAMDHENU or its equivalent (C.S.I. No. 9.03 ) | Qtl. | 10.56 | 6545.2 | 69117.312
6 | Providing and fixing of Dr. fixit LW+ in RCC/CC/PLASTER etc. 200ml per bag of cement as directed by E/I including supply of all material, labour and T&P etc. required for proper completion of work.(NSI) | Ltr | 23.23 | 128.5 | 2985.055
7 | 12mm thick plaster with cement mortar consisting of one par of cement and three part of coarse sand (1:3) minimum thickness not to be less then 10mm including supply of all material, labour and T&P etc. for proper completion of work. (CSI No. 11.06) | Sqm | 194.47 | 175 | 34032.25
8 | 3 mm thick floating coat of neat cement finish including supply of all material, labour and T&P etc. required for proper completion of the work. (Cement consumtion 0.044bag/Sqm.) (CSI No. 11.20+0.044x11.15) | Sqm. | 102.64 | 23.07 | 2367.9048
9 | 1st Class brick ( class-150) work in 1:6 cement and coarse sand (F.M. 1.8.to 2.5 ). mortar in super structure including supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.6.01+6.07+6.08) | Cum. | 2.89 | 5763 | 16655.07
10 | Providing and fixing of 110 mm dia PVC Pipe 6 kg/sq.cm for with special such as Tee, bend, socket, elbow etc including supply of all labour , material T&P etc. complete required for proper completion of the work. (CSI No. 26.17) | Rm | 23.89 | 249 | 5948.61
11 | Dismantiling existing plaster including disposal of refuse as directed by the E/C with in a distance of 60M.(C.S.I.No.15.11) | Sqm | 590.63 | 32 | 18900.16
12 | 12mm thick plaster with cement mortar consisting of one par of cement and four part of coarse sand (1: 4) minimum thickness not to be less then 10mm including supply of all material, labour and T&P etc. for proper completion of work. (CSI No. 11.07) | Sqm | 226.81 | 158 | 35835.98
13 | 12 mm (1/2") thick plaster with cement mortar consisting of one part of cement and 6 part of coarse sand (1:6), minium thickness not to be less then 10mm including suply of all materials, labour and T&P etc. for proper completion of the work.(CSI.NO.11.09) | Sqm. | 207.69 | 148 | 30738.12
14 | Painting two coat with Acrylic/synthetic distemper of Berger/Asian over new wall interior surface over one priming coat cement primer (water based) of ICI or equivalent make as approved by E/I including supply of all materials, labour & T&P etc. required .(C.S.I.No. 13.25+13.26) | Sqm. | 239.93 | 106 | 25432.58
15 | White washing three coat including cost of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.14.03) | Sqm. | 91.83 | 14 | 1285.62
16 | Finishing of walls with water proof exterior emulsion paint of ACE of Asian paints or equialent make including 3 coats of above paint including one priming coat on already well prepared new wall surface to give an even shade including cost of all materials, labour and T&P egc. complete for proper completion of the work.(NSI) | Sqm. | 222.18 | 80 | 17774.4
17 | Dismantiling cement concrete or brick or grnolithic floors including base concrete and including stacking of dismantled materials as directed by the E/I. with in a distance 60M.(C.s.I.No.15.05) | Sqm | 133.27 | 44 | 5863.88
18 | Clearing of septic tank including disposal of waste out side the UPPCL area as per direction of the E/I. including cost of all labour T&P etc. required for proper completion of the work.(CSI No. 20.12) | N0 | 1 | 1348 | 1348
19 | 40 mm. thick C.C. 1:2:4 plain cement concrete floor with cement, approved coarse sand, and 2cm.(3/4") graded approved stone ballast laid in pannels finished with 3mm.(1/8") floating coat of neat cement or cement and marble dust in ratio of 5:1 as specified over and removing any over lapping mortar at the joints of the pannels, if any, and giving them a uniform finish including supply of all materials labour and T&P etc. required for proper completion of the work with without base concrete.(C.S.I.No.12.04) | Sqm. | 96.76 | 375 | 36285
20 | Providing and fixing glass strips of 3.15 mm thickness & 40mm depth in joints of floor and skriting at the time of laying floors, flush with floor level including supply of labour T&P etc. required for proper completion of the work. (C.S.I. No. 12.14) | Rm | 319 | 28 | 8932
21 | 1st Class brick ( class-150) work in 1:6 cement and coarse sand (F.M. 1.5.to 2.0 ). mortar in foundation and plinth including supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.6.01) | Cum. | 12.23 | 5205 | 63657.15
22 | Concrete with 4cm gauge stone ballast coarse sand ( F.M. 1.8 to 2.5) & cement in proportion of 12:6:1 in foundation & under floors including supply of all materials, labour and T&P etc. required for proper completion of work.(CSI No. 5.02) | Cum. | 30.46 | 4167 | 126926.82
23 | Local river sand filling in plinth including supply of necessary quantity of sand from a distances not exceeding 8 Kms. (5 miles) from the site of work including watering ramming and dressing etc. Rate include cost of all materials, labour and T & P etc. required for proper completion of the work.(C.S.I. No. 4.05) | Cum. | 40 | 587 | 23480
24 | Supply and Laying 8 mm thick glazed floor tiles of Somany, Johnson or equivalent make, of size 300x300 mm, laid with 1:3 cement and approved coarse sand mortar finished with white cement slurry, jointing and polishing complete, including supply of all materials, labour and T&P etc. completion required for proper completion of the work. (CSI No. 12.11) | Sqm | 4.29 | 1165 | 4997.85
25 | Supply and Laying 6 mm thick glazed tiles of size 200x300 mm in skirting / dado laid with 1:3 cement and approved coarse sand mortar finished with white cement slurry, jointing and polishing complete,including supply of all materials, labour and T&P etc. completion required for proper completion of the work. (CSI No. 12.12) | Sqm | 13.95 | 1000 | 13950
26 | Providing and fixing white glazed China earthen ware water closet squatting " Orisa type" pan weaper size 580mmx140mm Hindustan Make or other equivalent approved make of Ist quality with 100mm dia. White glazed P or S trap fittings including cutting & making good the walls and floors wherever required with cement sand and grit mortar not less than 1:4 the seat and trap shall have to be fixed over minimum 3" thick c.c. in proportion of 12:6:1 including cost of all materials, labour(C.S.I.No. 27.01+27.23) | Nos. | 1 | 2891 | 2891
27 | Dismantling of doors or window chowkhats including stacking of materials as directed by the E/I. within a distance of 60M.(CSI No. 15.10) | Sqm | 19.62 | 57 | 1118.34
28 | Supply and fixing of 32 mm thick single leaf flush door shutter (boiled water resistaance, phenol maldehide resin bonded, hot pressed factory made ( commercial quality to I.S. 2202 part-1 (1993) ISI marked including fixing of wooden leats and stoppers and including fixing and adjustment of hinges bolts, lokcs, handles, springs and other fitting but excluding their supply including all materials, labour & T&P etc. required for proper completion of work. ( CSI No. 8.57) | Sqm. | 10.64 | 1559 | 16587.76
29 | Mild steel or iron work in heavy sizes such as trusses built-up gates, door frames, record, racks, roof work, gates etc. wrought to required form including holes rivetting or welding where necessary and also fixing in proper position and alignment including cost of all materials supplied by contractor (CSI No. 9.01 ) | Qtl. | 12.23 | 7491.9 | 91625.937
30 | Supply and fixing galvanised mosquito proof jali ( 16x24 gauge ) with M.S. flat of 20x3mm. Size on both sides screwed or welded to window or door frame.(CSI No. 9.18) | Sqm | 11.23 | 582 | 6535.86
31 | Providing and fixing steel glazed window and ventilators of standard rolled Mann or mahavir steel section conforming to IS 7452-1974 as per drawing joints metered & welded with 100x14x3.15mm holdfast embedded in cement conctete block 15x10x10 cm. size of 1:3:6 proportion I.E. First part of cement 3 part of approved coarse sand & 6 part of graded stone (aggregated 20mm. Nominal size) S/F of glass panes of plain pin headed 4mm. Thick nuts glazing clips and special putty of approved make complete and including a cost of red oxide paint. The fabrication should conform to I.S. 1038-1975 ( Aluminum beading with rubber packing included) (CSI No. 9.17) | Sqm | 11.23 | 3828 | 42988.44
32 | Painting or varnishing new iron works or new wood work with one coat of ready mixed priming paint and two coats of approved superior quality ready mixed enamel paint 'LUXOL' or equivalent brand or varnish including supply of all materials, labour& T&P etc. required for proper completion of the work (C.S.I. No. 13.01+13.02) | Sqm. | 67.14 | 97 | 6512.58
33 | Pre-Construction anti-termite treatment, by breating a barrier under and around the coloumns pits, foundation trenches, under floors, junctions of walls & floors, around the external perimetre of building, expansion, joints, surrounding of pipes and coduits etc.(Plinth area of the building at ground floor only shall be measured as per I.S. 6313 ( Part II 1981 ) with Aldine exulsifiable 0.2% concentration or any other approved material such as Heptachlore or chlordance will be used. The consumption of emulsion shall be (i) Foundation and masonary @ 5 Ltrs /Sqm (ii) Back fills in immediate contact of foundation@ 7.5 Ltrs/Sqm ((iii) Top surface of plinth filling @ 5 Ltrs/Sqm,(iv) junction of walls & floors @ 7.5 Ltrs/Sqm (v) Soil along extermal perlimetre of building @ 7.5 Ltrs/Sqm(vi) under apron of the building @ 5 Ltrs/Sqm. The rates includes cost of all materials, labour, equipments, T&P complete.(CSI No. 17.01) | Sqm | 91.83 | 82 | 7530.06
34 | Concrete with 20mm. (1.5") gauge approved hard Stone ballast, coarse sand of ( F.M.1.5 to 2.0) and cement in proportion of 4:2:1in foundation and under floors and supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. NO. 5.06) | Cum. | 0.57 | 6386 | 3640.02
35 | Clearing jungle including uprooting of rank vegetations grass, bush, wood, trees and saplings of girth up to 30cm measured at a height of 1.0m above ground level and removal of rubbish up to a distance of 50m outside the periphery of UPPCL area cleared.(CSI No. 4.08) | Sqm | 150 | 5 | 750
36 | Providing and Fixing barbed iron wire wire fencing including stretching, fixing in to the post including all labour, materials and T&P required for proper completion of work the weight of hot dipped GI barbed wire having 12 SWG-2 ply wires and 4 point ordinary barbs @ 150mm (approx ) C/C should be 100 gm per Meter.(CSI No. 9.07) | Rmt. | 90 | 11 | 990
37 | Excavation in foundation in ordinary soil (Loam Clay or Sand) including lift upto 1.5 meter and lead upto 30 meter and including filling , watering, and ramming of excavated earth into the trenches or into the space between the building and sides of the foundation the work . (C.S.I. No 4.01) | Cum. | 7.2 | 133 | 957.6
38 | Disposal of rubbish/debris out side the UPPCL area as per direction of E/I. including cartage, labour and materials, T&P etc. required for proper completion of the work. ( No deduction for voids shall be made ) ( CSI No. 20.16). | Cum. | 15.4 | 264 | 4065.6
39 | First class brick ( Class-150) laid dry in foundation and plinth as in circular sockpit walls of one brick thickness and 2.0 to 3.0M depth including cutting moulding bricks as required including cost of all materials, labour and T&P complete (CSI No. 6.16) | Cum. | 0.8 | 4749 | 3799.2
40 | Providing and laying floor of 10mm thick industrial (heavy duty) tiles in flooring or skirting of approved brand ( Bell, Johnson or equil, make) size of 300x300mm of approved shade, clour and pattern, laid over base cement mortar 1:4 mix icluding finishing the joints with white cement mixed with pigment to match the shade of tile including cost of all material, labour and T&P required for proper completion of the work.( NSI) | Sqm | 50 | 1728 | 86400
41 | Add for extra labour and materials for plaster over rough face of one brick thick wall.(CSI No. 11.12) | Sqm | 220 | 20 | 4400
42 | Firs class bricks on edge floor laid dry joints sand filed including preparation of base to proper slope and its ramming including supply of all material labour & T&P etc. required for proper completion of the work.(CSI No. 12.07) | Sqm | 40 | 558 | 22320
43 | Providing and fixing 1mm thick M.S. sheet garrage door with frame of 40x40x6mm angle iron, diagonal bracings with 50x5 mm flat and 5mm thick M.S.gusset plates at the junctions and corner including supply and fixing of necessary fitting 2 no. lock rail of 16 dia , 375mm long and including pintel hooks at the top and bottom, applying a priming coat of red oxide paint on all sides complete. (CSI No.9.34) | Sqm | 1.24 | 3002 | 3722.48
44 | Removal of cement mortar from dismenttled bricks and stacking in countable position at place as directed by the E/I. including cost of all labour and T&P required for proper completion of work. (CSI No. 6.22) | Cum. | 6.64 | 989 | 6566.96
45 | Providing and fixing of India Marka 2 hand pupms |  |  |  | 0
Boring in all type of Strata to make 110mm dia bore hole and development of bore hole till clean water is obtained .
(a) | S/F of India marka-II hand pump complete. | Rm. | 1 | 5380 | 5380
(b) | Supply and Loweing PVC 110mm dia heavy quality pipe. | Rm. | 40 | 250 | 10000
( C) | Supply and Lowering of 1.5" dia G.I. pipe B | Rm. | 20 | 202.9 | 4058
(d) | S/F of 12mm dia connecting rod. | Rm. | 8 | 200 | 1600
(e) | Boring for110mm dia bore hole . | Rm. | 45 | 1201 | 54045
(f) | Filling of Ventonite material | Job | 1 | 500 | 500
(g) | Devloping of hand pump | P/H | 5 | 600 | 3000
(h) | Cortage of materials | Job | 1 | 1800 | 1800
46 | Wiring point for light with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch & ceiling rose /single/batten holder on 3mm. thick phenolic laminated backelite sheet etc. complete in all respect, as directed including matching colour wash (PSI N0 131(C ) | Nos. | 10 | 518 | 5180
47 | Wiring point for fan /fresh air fan with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch & ceiling rose on 3mm. thick phenolic laminated backelite sheet etc. complete in all respect, as directed including matching colour wash(PSI N0.133( C) | NO | 4 | 595 | 2380
48 | Wiring point for plug with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch and socket etc.complete in all respect, including matching colour wash((PSI N0.134(C ) | NO | 5 | 275 | 1375
49 | Wiring point for exhaust fan with 1.5sq.mm FR PVC insulated multistrand single core copper conductor cable in PVCl conduit concealed in the wall, complete with 14 SWG copper earth continuity wire and 15 A piano type ceiling rose on 3mm thick phenolic laminated backelite sheet etc. complete in all respect including matching colour wash (PSI No. 137 (C ) | No. | 3 | 780 | 2340
50 | S/F of LED fluorescent tube light fitting suitable for 1x18 watt fluorescent tube complete including tubes etc. on surface complete in all respects.(NSI) | Each | 10 | 1100 | 11000
51 | Supply and fixing of high speed ceiling fan 1200mm size of USHA or any approved make by E/I. complet in all respect (NSI) | No. | 4 | 1686 | 6744
52 | S/F of MCB ( 6-32Amp) PSI 1002 CAT-A | No | 8 | 250 | 2000
53 | S&F surface/flush mounting 12 ways SPN distribution board ( Legrand Lexic ) with additional metal door without MCB complete in all respect, as directed at site by E/I (PSI N0.1025A) | No | 1 | 2100 | 2100
54 | S/F of electronic fan dimmer, 120-280V , ISI marked on the existing switch board including making connnection, required material, labour T&P egc. For proper completion of work to the satisfaction of E/I. of work (PSI 1203(A) | No. | 4 | 305 | 1220
55 | Supply and fixing of power plug with 20A/250 volt flush type switch and 5 pin 20A/250V flush type universal socket in suitable M.S. box of 175mmx100mmx50mm size with phenoic laminated bakelite sheet cover 3mm thick fixed with brass machinne screw and cup washer (PSI N0.1139) (A) | No. | 4 | 595 | 2380
56 | S& F of Electrical (Porcelain) Cut Out 63Amp as directed by E/I(NSI) | No. | 4 | 300 | 1200
57 | supply and burying of 600mmx600mmx6mm GI plate vertically for earthing with its top at least 3 metres below ground tevel complete with 20mm dia g.I. pipe and funned for watering and one eahing lead of one no. 8 to 10 SWG copper wire in 15mm dia G.I.pipe up to switch board (From appron to switch board the cost of G.I. pipe and G.I. wire will be extra) 30cm square C.I. frame with hinged cover masonry housing alternate layers of charcoal/coke and salt at least 150mm thick alround etc. as per direction of E/I. complete in all respect\ (PSI N0 703) | No. | 1 | 4730 | 4730
58 | 63Amp.Double Pole Isolator (Legrand Lexic) (PSI N0 1005B) | No | 1 | 590 | 590
59 | S&F hexagonal fan box with hexagonal side of approx 80mm in length fabricated from 16 SWG MS sheet incorporating 10mm dia M.S. round bar duly bent for supporting fan hanger duly painted withred oxide and screwing arrangement with wiring conduit laid in the RCC roof before concreting along with supply of all material, labour and T&P etc. required for proper completion of the work (PSI No. 1149) | No. | 4 | 135 | 540
60 | Supply and wiring of submain with two number 4 sq.mm in PVC insulated 1100V grade multistrand single core copper conductor cable in 20 mm dia heavy duty (2mm thick)PVC conduit concealed in wall, complete with one number 2.5 sqmm. copper cable as earth continuity wire etc. complet in all respect (PSI No. 216 ( C ) | Rm | 200 | 155 | 31000
61 | Supply and wiring of submain with two number 6 sq.mm in PVC insulated 1100V grade multistrand single core copper conductor cable in 25 mm dia heavy duty (2mm thick)PVC conduit concealed in wall, complete with one number 4.00 sqmm. copper cable as earth continuity wire etc. complet in all respect (PSI No. 217( C ) | Rm | 50 | 215 | 10750
62 | supply and wiring of submain with two number 2.5 sq.mm. FR PVC insulated 1100 V grade multistrand single core copper conductor cable in 20mm dia heavy duty (2mm thick) PVC conduit with 1 number 1.5 sq.mm. FR PVCearth continuity wire complete in all respect including matching colour wash etc. complete in all respect.(PSI No. 1304C) | Rm | 200 | 121 | 24200
63 | supply and wiring of submain with two number 1.5 sq.mm. FR PVC insulated 1100 V grade multistrand single core copper conductor cable in 20mm dia heavy duty (2mm thick) PVC conduit with one number 1.5 sq.mm. FR PVC earth continuity wire complete in all respect including matching colour wash etc. complete in all respect .(PSI No. 1312C) | Rm | 50 | 104 | 5200
64 | S/F of 16 gauge M.S. drum duly painted included making hole in the wall for exhaust fan and finishing proporely complete in all respcet.(PSI No. 1122) | No. | 4 | 680 | 2720
65 | Making hole in the wall for exhaust fan and finishing properly complete in all respect (PSI N0.1121) | No. | 1 | 325 | 325
66 | Supply and fixing of factor fabricated M.S. box in existing sunk of size 600mmx480mmx200mm deep with Godrej type almirah, cover with handle etc. fabricated from 18 SWG ( 1.25mm) M.S. sheet duly painted with red oxide primer followed by two coats of synthetic enamet paint complete with necessary conduit entry and D.P. /T.P.N; fixing arrangement and provision for compartment for loose wires openable housing on the top and hold fast etc. including supply of all material., labour T&P etc. required for proper completion of the work.(PSI No. 1147) | No. | 1 | 1435 | 1435
67 | Supply and fixing of 12inch high speed exhaust fan make-USHA, havels etc or its equivalent including, labour, materials and T&P complete in all respect as directed by E/I. (NSI) | No | 3 | 1686 | 5058
68 | S/F of switch box made up to 16SWG (1.5mm) thick M.S. sheet of 100x100x65mm size duly painted with red oxide primer and flushed in wall ineluding cutting of brick work, fixing it to the level with cement sand mortar, including matching colour wash with s/o all materials, labour and T&P required for proper completion of work as directed a site by the E/I.(PSI No. 159) | No | 2 | 60 | 120
69 | Same as item no 68.but of 150x150x65mm size (PSI No.160) | No | 2 | 95 | 190
70 | Same as item no 68 .but of 175x250x65mm size (PSI No.161) | No | 2 | 90 | 180
71 | Same as item no.68 .but of 200x250x65mm size (PSI No.162) | No | 2 | 145 | 290
72 | Same as item no.68 .but of 250x250x65mm size (PSI No.163) | No | 2 | 165 | 330
73 | Construction of recess of 600mmx480mmx200mm size of main boards, distribution boards of all sizes including cutting of brick work, providing lintel of suitable size and thickness, plastering etc. with supply of all materials, labour T&P required for proper completion of work.(PSI No.1141B) | No. | 1 | 480 | 480
| Total |  |  |  | 1203817.5688
| Jr. Engr. | S.D.O |  | Ex. Engineer

## PARA
APPROXIMATE BILL OF QUANTITY FOR M&R OF MISC. CIVIL WORKS
AT 33/ 11 K.V. PARA, GHAZIPUR
Sl. | ITEM OF WORKS | UNIT | QUANTITY | RATE | AMOUNT
1 | 2 | 3 | 4 | 5 | 6
1 | Dismantiling of existing damaged Mud Faska over the roof. Cleaning the surface with wire brush, removal and disposal of rubbish at a distance 100 meters also including the cost of celaning and stacking of usable materials etc. including all labour, material required for porper completion of work.(CSI No. 15.14) | Sqm | 99.5 | 107 | 10646.5
2 | Dismantling brick work or stone work in lime or cement mortar and including stacking of materials as directied by the E/I. within a distance of 60 metres. (CSI.No.15.01) | Cum. | 2.5 | 389 | 972.5
3 | Providing of Dr. fixit 301 pidicrete URP & mixing it properly with cement in the proportion of 1:1.5 apply two coat to the prepared surface including cost of labour, material T&P etc. as required for proper completion of work as directed by E/I.(NSI) | Sqm | 99.5 | 262 | 26069
4 | R.C.C. work with cement, approved coarse sand and 2 cm. (3/4") gauge approved stone ballast in the proportion of 1:1.5:3 in the SLABS excluding reinforcement and its bending but including its fixing and binding the same with 24 BWG, G.I. binding wire and including necessary centering and shuttering etc. and also including supply of all materials, labour and T&P etc. required for proper completion of the work. (Binding wire to be supplied by the contractor free of cost).(C.S.I. No. 5.24) | Cum. | 3.5 | 9117 | 31909.5
5 | Mild steel of or iron in plain work such as reinforced concrete or reinforced brick work. (when not included in over all rates) wrought to required shape as necessary including bending for proper completion of the work and including supply of steel, its wastage, bend hooks, and authorized overlapping shall be measured. Rainforcement steel of tensile strength 415 N/MM² steel, TMT steel rods of TATA/ SAIL/KAMDHENU or its equivalent (C.S.I. No. 9.03 ) | Qtl. | 2.34 | 6545.2 | 15315.768
6 | Providing and fixing of Dr. fixit LW+ in RCC/CC/PLASTER etc. 200ml per bag of cement as directed by E/I including supply of all material, labour and T&P etc. required for proper completion of work.(NSI) | Ltr | 14.87 | 128.5 | 1910.795
7 | 12mm thick plaster with cement mortar consisting of one par of cement and three part of coarse sand (1:3) minimum thickness not to be less then 10mm including supply of all material, labour and T&P etc. for proper completion of work. (CSI No. 11.06) | Sqm | 135.23 | 175 | 23665.25
8 | 3 mm thick floating coat of neat cement finish including supply of all material, labour and T&P etc. required for proper completion of the work. (Cement consumtion 0.044bag/Sqm.) (CSI No. 11.20+0.044x11.15) | Sqm. | 99.5 | 23.07 | 2295.465
9 | 1st Class brick ( class-150) work in 1:6 cement and coarse sand (F.M. 1.8.to 2.5 ). mortar in super structure including supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.6.01+6.07+6.08) | Cum. | 2.5 | 5763 | 14407.5
10 | Providing and fixing of 110 mm dia PVC Pipe 6 kg/sq.cm for with special such as Tee, bend, socket, elbow etc including supply of all labour , material T&P etc. complete required for proper completion of the work. (CSI No. 26.17) | Rm | 20 | 249 | 4980
11 | Dismantiling existing plaster including disposal of refuse as directed by the E/C with in a distance of 60M.(C.S.I.No.15.11) | Sqm | 315 | 32 | 10080
12 | 12mm thick plaster with cement mortar consisting of one par of cement and four part of coarse sand (1: 4) minimum thickness not to be less then 10mm including supply of all material, labour and T&P etc. for proper completion of work. (CSI No. 11.07) | Sqm | 90.7 | 158 | 14330.6
13 | 12 mm (1/2") thick plaster with cement mortar consisting of one part of cement and 6 part of coarse sand (1:6), minium thickness not to be less then 10mm including suply of all materials, labour and T&P etc. for proper completion of the work.(CSI.NO.11.09) | Sqm. | 119.3 | 148 | 17656.4
14 | Painting two coat with Acrylic/synthetic distemper of Berger/Asian over new wall interior surface over one priming coat cement primer (water based) of ICI or equivalent make as approved by E/I including supply of all materials, labour & T&P etc. required .(C.S.I.No. 13.25+13.26) | Sqm. | 130 | 106 | 13780
15 | White washing three coat including cost of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.14.03) | Sqm. | 85 | 14 | 1190
16 | Finishing of walls with water proof exterior emulsion paint of ACE of Asian paints or equialent make including 3 coats of above paint including one priming coat on already well prepared new wall surface to give an even shade including cost of all materials, labour and T&P egc. complete for proper completion of the work.(NSI) | Sqm. | 145 | 80 | 11600
17 | Dismantiling cement concrete or brick or grnolithic floors including base concrete and including stacking of dismantled materials as directed by the E/I. with in a distance 60M.(C.s.I.No.15.05) | Sqm | 118.78 | 44 | 5226.32
18 | Clearing of septic tank including disposal of waste out side the UPPCL area as per direction of the E/I. including cost of all labour T&P etc. required for proper completion of the work.(CSI No. 20.12) | N0 | 1 | 1348 | 1348
19 | 40 mm. thick C.C. 1:2:4 plain cement concrete floor with cement, approved coarse sand, and 2cm.(3/4") graded approved stone ballast laid in pannels finished with 3mm.(1/8") floating coat of neat cement or cement and marble dust in ratio of 5:1 as specified over and removing any over lapping mortar at the joints of the pannels, if any, and giving them a uniform finish including supply of all materials labour and T&P etc. required for proper completion of the work with without base concrete.(C.S.I.No.12.04) | Sqm. | 72.23 | 375 | 27086.25
20 | Providing and fixing glass strips of 3.15 mm thickness & 40mm depth in joints of floor and skriting at the time of laying floors, flush with floor level including supply of labour T&P etc. required for proper completion of the work. (C.S.I. No. 12.14) | Rm | 158.67 | 28 | 4442.76
21 | 1st Class brick ( class-150) work in 1:6 cement and coarse sand (F.M. 1.5.to 2.0 ). mortar in foundation and plinth including supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.6.01) | Cum. | 2.44 | 5205 | 12700.2
22 | Concrete with 4cm gauge stone ballast coarse sand ( F.M. 1.8 to 2.5) & cement in proportion of 12:6:1 in foundation & under floors including supply of all materials, labour and T&P etc. required for proper completion of work.(CSI No. 5.02) | Cum. | 4 | 4167 | 16668
23 | Local river sand filling in plinth including supply of necessary quantity of sand from a distances not exceeding 8 Kms. (5 miles) from the site of work including watering ramming and dressing etc. Rate include cost of all materials, labour and T & P etc. required for proper completion of the work.(C.S.I. No. 4.05) | Cum. | 7.2 | 587 | 4226.4
24 | Supply and Laying 8 mm thick glazed floor tiles of Somany, Johnson or equivalent make, of size 300x300 mm, laid with 1:3 cement and approved coarse sand mortar finished with white cement slurry, jointing and polishing complete, including supply of all materials, labour and T&P etc. completion required for proper completion of the work. (CSI No. 12.11) | Sqm | 3.2 | 1165 | 3728
25 | Supply and Laying 6 mm thick glazed tiles of size 200x300 mm in skirting / dado laid with 1:3 cement and approved coarse sand mortar finished with white cement slurry, jointing and polishing complete,including supply of all materials, labour and T&P etc. completion required for proper completion of the work. (CSI No. 12.12) | Sqm | 7.8 | 1000 | 7800
26 | Providing and fixing white glazed China earthen ware water closet squatting " Orisa type" pan weaper size 580mmx140mm Hindustan Make or other equivalent approved make of Ist quality with 100mm dia. White glazed P or S trap fittings including cutting & making good the walls and floors wherever required with cement sand and grit mortar not less than 1:4 the seat and trap shall have to be fixed over minimum 3" thick c.c. in proportion of 12:6:1 including cost of all materials, labour(C.S.I.No. 27.01+27.23) | Nos. | 1 | 2891 | 2891
27 | Dismantling of doors or window chowkhats including stacking of materials as directed by the E/I. within a distance of 60M.(CSI No. 15.10) | Sqm | 17.5 | 57 | 997.5
28 | Supply and fixing of 32 mm thick single leaf flush door shutter (boiled water resistaance, phenol maldehide resin bonded, hot pressed factory made ( commercial quality to I.S. 2202 part-1 (1993) ISI marked including fixing of wooden leats and stoppers and including fixing and adjustment of hinges bolts, lokcs, handles, springs and other fitting but excluding their supply including all materials, labour & T&P etc. required for proper completion of work. ( CSI No. 8.57) | Sqm. | 3.2 | 1559 | 4988.8
29 | Mild steel or iron work in heavy sizes such as trusses built-up gates, door frames, record, racks, roof work, gates etc. wrought to required form including holes rivetting or welding where necessary and also fixing in proper position and alignment including cost of all materials supplied by contractor (CSI No. 9.01 ) | Qtl. | 3.98 | 7491.9 | 29817.762
30 | Supply and fixing galvanised mosquito proof jali ( 16x24 gauge ) with M.S. flat of 20x3mm. Size on both sides screwed or welded to window or door frame.(CSI No. 9.18) | Sqm | 4.02 | 582 | 2339.64
31 | Providing and fixing steel glazed window and ventilators of standard rolled Mann or mahavir steel section conforming to IS 7452-1974 as per drawing joints metered & welded with 100x14x3.15mm holdfast embedded in cement conctete block 15x10x10 cm. size of 1:3:6 proportion I.E. First part of cement 3 part of approved coarse sand & 6 part of graded stone (aggregated 20mm. Nominal size) S/F of glass panes of plain pin headed 4mm. Thick nuts glazing clips and special putty of approved make complete and including a cost of red oxide paint. The fabrication should conform to I.S. 1038-1975 ( Aluminum beading with rubber packing included) (CSI No. 9.17) | Sqm | 4.02 | 3828 | 15388.56
32 | Painting or varnishing new iron works or new wood work with one coat of ready mixed priming paint and two coats of approved superior quality ready mixed enamel paint 'LUXOL' or equivalent brand or varnish including supply of all materials, labour& T&P etc. required for proper completion of the work (C.S.I. No. 13.01+13.02) | Sqm. | 30.23 | 97 | 2932.31
33 | Pre-Construction anti-termite treatment, by breating a barrier under and around the coloumns pits, foundation trenches, under floors, junctions of walls & floors, around the external perimetre of building, expansion, joints, surrounding of pipes and coduits etc.(Plinth area of the building at ground floor only shall be measured as per I.S. 6313 ( Part II 1981 ) with Aldine exulsifiable 0.2% concentration or any other approved material such as Heptachlore or chlordance will be used. The consumption of emulsion shall be (i) Foundation and masonary @ 5 Ltrs /Sqm (ii) Back fills in immediate contact of foundation@ 7.5 Ltrs/Sqm ((iii) Top surface of plinth filling @ 5 Ltrs/Sqm,(iv) junction of walls & floors @ 7.5 Ltrs/Sqm (v) Soil along extermal perlimetre of building @ 7.5 Ltrs/Sqm(vi) under apron of the building @ 5 Ltrs/Sqm. The rates includes cost of all materials, labour, equipments, T&P complete.(CSI No. 17.01) | Sqm | 60.24 | 82 | 4939.68
34 | Concrete with 20mm. (1.5") gauge approved hard Stone ballast, coarse sand of ( F.M.1.5 to 2.0) and cement in proportion of 4:2:1in foundation and under floors and supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. NO. 5.06) | Cum. | 0.57 | 6386 | 3640.02
35 | Clearing jungle including uprooting of rank vegetations grass, bush, wood, trees and saplings of girth up to 30cm measured at a height of 1.0m above ground level and removal of rubbish up to a distance of 50m outside the periphery of UPPCL area cleared.(CSI No. 4.08) | Sqm | 150 | 5 | 750
36 | Providing and Fixing barbed iron wire wire fencing including stretching, fixing in to the post including all labour, materials and T&P required for proper completion of work the weight of hot dipped GI barbed wire having 12 SWG-2 ply wires and 4 point ordinary barbs @ 150mm (approx ) C/C should be 100 gm per Meter.(CSI No. 9.07) | Rmt. | 85 | 11 | 935
37 | Excavation in foundation in ordinary soil (Loam Clay or Sand) including lift upto 1.5 meter and lead upto 30 meter and including filling , watering, and ramming of excavated earth into the trenches or into the space between the building and sides of the foundation the work . (C.S.I. No 4.01) | Cum. | 2.5 | 133 | 332.5
38 | Disposal of rubbish/debris out side the UPPCL area as per direction of E/I. including cartage, labour and materials, T&P etc. required for proper completion of the work. ( No deduction for voids shall be made ) ( CSI No. 20.16). | Cum. | 10.4 | 264 | 2745.6
39 | First class brick ( Class-150) laid dry in foundation and plinth as in circular sockpit walls of one brick thickness and 2.0 to 3.0M depth including cutting moulding bricks as required including cost of all materials, labour and T&P complete (CSI No. 6.16) | Cum. | 0.8 | 4749 | 3799.2
40 | Providing and laying floor of 10mm thick industrial (heavy duty) tiles in flooring or skirting of approved brand ( Bell, Johnson or equil, make) size of 300x300mm of approved shade, clour and pattern, laid over base cement mortar 1:4 mix icluding finishing the joints with white cement mixed with pigment to match the shade of tile including cost of all material, labour and T&P required for proper completion of the work.( NSI) | Sqm | 40 | 1728 | 69120
41 | Add for extra labour and materials for plaster over rough face of one brick thick wall.(CSI No. 11.12) | Sqm | 220 | 20 | 4400
42 | Firs class bricks on edge floor laid dry joints sand filed including preparation of base to proper slope and its ramming including supply of all material labour & T&P etc. required for proper completion of the work.(CSI No. 12.07) | Sqm | 15 | 558 | 8370
43 | Providing and fixing 1mm thick M.S. sheet garrage door with frame of 40x40x6mm angle iron, diagonal bracings with 50x5 mm flat and 5mm thick M.S.gusset plates at the junctions and corner including supply and fixing of necessary fitting 2 no. lock rail of 16 dia , 375mm long and including pintel hooks at the top and bottom, applying a priming coat of red oxide paint on all sides complete. (CSI No.9.34) | Sqm | 3.2 | 3002 | 9606.4
44 | Removal of cement mortar from dismenttled bricks and stacking in countable position at place as directed by the E/I. including cost of all labour and T&P required for proper completion of work. (CSI No. 6.22) | Cum. | 6.64 | 989 | 6566.96
45 | Wiring point for light with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch & ceiling rose /single/batten holder on 3mm. thick phenolic laminated backelite sheet etc. complete in all respect, as directed including matching colour wash (PSI N0 131(C ) | Nos. | 10 | 518 | 5180
46 | Wiring point for fan /fresh air fan with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch & ceiling rose on 3mm. thick phenolic laminated backelite sheet etc. complete in all respect, as directed including matching colour wash(PSI N0.133( C) | NO | 4 | 595 | 2380
47 | Wiring point for plug with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch and socket etc.complete in all respect, including matching colour wash((PSI N0.134(C ) | NO | 5 | 275 | 1375
48 | Wiring point for exhaust fan with 1.5sq.mm FR PVC insulated multistrand single core copper conductor cable in PVCl conduit concealed in the wall, complete with 14 SWG copper earth continuity wire and 15 A piano type ceiling rose on 3mm thick phenolic laminated backelite sheet etc. complete in all respect including matching colour wash (PSI No. 137 (C ) | No. | 3 | 780 | 2340
49 | S/F of LED fluorescent tube light fitting suitable for 1x18 watt fluorescent tube complete including tubes etc. on surface complete in all respects.(NSI) | Each | 10 | 1100 | 11000
50 | Supply and fixing of high speed ceiling fan 1200mm size of USHA or any approved make by E/I. complet in all respect (NSI) | No. | 4 | 1686 | 6744
51 | S/F of MCB ( 6-32Amp) PSI 1002CAT-A | No | 8 | 250 | 2000
52 | S&F surface/flush mounting 12 ways SPN distribution board ( Legrand Lexic ) with additional metal door without MCB complete in all respect, as directed at site by E/I (PSI N0.1025A) CAT-A | No | 1 | 2100 | 2100
53 | S/F of electronic fan dimmer, 120-280V , ISI marked on the existing switch board including making connnection, required material, labour T&P egc. For proper completion of work to the satisfaction of E/I. of work (PSI 1203(A) | No. | 4 | 305 | 1220
54 | Supply and fixing of power plug with 20A/250 volt flush type switch and 5 pin 20A/250V flush type universal socket in suitable M.S. box of 175mmx100mmx50mm size with phenoic laminated bakelite sheet cover 3mm thick fixed with brass machinne screw and cup washer (PSI N0.1139) (A) | No. | 4 | 595 | 2380
55 | S& F of Electrical (Porcelain) Cut Out 63Amp as directed by E/I(NSI) | No. | 4 | 300 | 1200
56 | supply and burying of 600mmx600mmx6mm GI plate vertically for earthing with its top at least 3 metres below ground tevel complete with 20mm dia g.I. pipe and funned for watering and one eahing lead of one no. 8 to 10 SWG copper wire in 15mm dia G.I.pipe up to switch board (From appron to switch board the cost of G.I. pipe and G.I. wire will be extra) 30cm square C.I. frame with hinged cover masonry housing alternate layers of charcoal/coke and salt at least 150mm thick alround etc. as per direction of E/I. complete in all respect\ (PSI N0 703) | No. | 1 | 4730 | 4730
57 | 63Amp.Double Pole Isolator (Legrand Lexic) (PSI N0 1005B) | No | 1 | 590 | 590
58 | S&F hexagonal fan box with hexagonal side of approx 80mm in length fabricated from 16 SWG MS sheet incorporating 10mm dia M.S. round bar duly bent for supporting fan hanger duly painted withred oxide and screwing arrangement with wiring conduit laid in the RCC roof before concreting along with supply of all material, labour and T&P etc. required for proper completion of the work (PSI No. 1149) | No. | 4 | 135 | 540
59 | Supply and wiring of submain with two number 4 sq.mm in PVC insulated 1100V grade multistrand single core copper conductor cable in 20 mm dia heavy duty (2mm thick)PVC conduit concealed in wall, complete with one number 2.5 sqmm. copper cable as earth continuity wire etc. complet in all respect (PSI No. 216 ( C ) | Rm | 200 | 155 | 31000
60 | Supply and wiring of submain with two number 6 sq.mm in PVC insulated 1100V grade multistrand single core copper conductor cable in 25 mm dia heavy duty (2mm thick)PVC conduit concealed in wall, complete with one number 4.00 sqmm. copper cable as earth continuity wire etc. complet in all respect (PSI No. 217( C ) | Rm | 50 | 215 | 10750
61 | supply and wiring of submain with two number 2.5 sq.mm. FR PVC insulated 1100 V grade multistrand single core copper conductor cable in 20mm dia heavy duty (2mm thick) PVC conduit with 1 number 1.5 sq.mm. FR PVCearth continuity wire complete in all respect including matching colour wash etc. complete in all respect.(PSI No. 1304C) | Rm | 200 | 121 | 24200
62 | supply and wiring of submain with two number 1.5 sq.mm. FR PVC insulated 1100 V grade multistrand single core copper conductor cable in 20mm dia heavy duty (2mm thick) PVC conduit with one number 1.5 sq.mm. FR PVC earth continuity wire complete in all respect including matching colour wash etc. complete in all respect .(PSI No. 1312C) | Rm | 50 | 104 | 5200
63 | S/F of 16 gauge M.S. drum duly painted included making hole in the wall for exhaust fan and finishing proporely complete in all respcet.(PSI No. 1122) | No. | 4 | 680 | 2720
64 | Making hole in the wall for exhaust fan and finishing properly complete in all respect (PSI N0.1121) | No. | 1 | 325 | 325
65 | Supply and fixing of factor fabricated M.S. box in existing sunk of size 600mmx480mmx200mm deep with Godrej type almirah, cover with handle etc. fabricated from 18 SWG ( 1.25mm) M.S. sheet duly painted with red oxide primer followed by two coats of synthetic enamet paint complete with necessary conduit entry and D.P. /T.P.N; fixing arrangement and provision for compartment for loose wires openable housing on the top and hold fast etc. including supply of all material., labour T&P etc. required for proper completion of the work.(PSI No. 1147) | No. | 1 | 1435 | 1435
66 | Supply and fixing of 12inch high speed exhaust fan make-USHA, havels etc or its equivalent including, labour, materials and T&P complete in all respect as directed by E/I. (NSI) | No | 3 | 1686 | 5058
67 | S/F of switch box made up to 16SWG (1.5mm) thick M.S. sheet of 100x100x65mm size duly painted with red oxide primer and flushed in wall ineluding cutting of brick work, fixing it to the level with cement sand mortar, including matching colour wash with s/o all materials, labour and T&P required for proper completion of work as directed a site by the E/I.(PSI No. 159) | No | 2 | 60 | 120
68 | Same as item no 67.but of 150x150x65mm size (PSI No.160) | No | 2 | 95 | 190
69 | Same as item no 67 .but of 175x250x65mm size (PSI No.161) | No | 2 | 90 | 180
70 | Same as item no.67 .but of 200x250x65mm size (PSI No.162) | No | 2 | 145 | 290
71 | Same as item no.67 .but of 250x250x65mm size (PSI No.163) | No | 2 | 165 | 330
72 | Construction of recess of 600mmx480mmx200mm size of main boards, distribution boards of all sizes including cutting of brick work, providing lintel of suitable size and thickness, plastering etc. with supply of all materials, labour T&P required for proper completion of work.(PSI No.1141B) | No. | 1 | 480 | 480
| Total |  |  |  | 584653.14
| Jr. Engr. | S.D.O |  | Ex. Engineer

## MAHANUR
APPROXIMATE BILL OF QUANTITY FOR M&R OF MISC. CIVIL WORKS
AT 33/ 11 K.V. MAHANAUR, GHAZIPUR
Sl. | ITEM OF WORKS | UNIT | QUANTITY | RATE | AMOUNT
1 | 2 | 3 | 4 | 5 | 6
1 | Dismantiling of existing damaged Mud Faska over the roof. Cleaning the surface with wire brush, removal and disposal of rubbish at a distance 100 meters also including the cost of celaning and stacking of usable materials etc. including all labour, material required for porper completion of work.(CSI No. 15.14) | Sqm | 167.89 | 107 | 17964.23
2 | Dismantling brick work or stone work in lime or cement mortar and including stacking of materials as directied by the E/I. within a distance of 60 metres. (CSI.No.15.01) | Cum. | 3.52 | 389 | 1369.28
3 | Providing of Dr. fixit 301 pidicrete URP & mixing it properly with cement in the proportion of 1:1.5 apply two coat to the prepared surface including cost of labour, material T&P etc. as required for proper completion of work as directed by E/I.(NSI) | Sqm | 167.89 | 262 | 43987.18
4 | R.C.C. work with cement, approved coarse sand and 2 cm. (3/4") gauge approved stone ballast in the proportion of 1:1.5:3 in the SLABS excluding reinforcement and its bending but including its fixing and binding the same with 24 BWG, G.I. binding wire and including necessary centering and shuttering etc. and also including supply of all materials, labour and T&P etc. required for proper completion of the work. (Binding wire to be supplied by the contractor free of cost).(C.S.I. No. 5.24) | Cum. | 14.25 | 9117 | 129917.25
5 | Mild steel of or iron in plain work such as reinforced concrete or reinforced brick work. (when not included in over all rates) wrought to required shape as necessary including bending for proper completion of the work and including supply of steel, its wastage, bend hooks, and authorized overlapping shall be measured. Rainforcement steel of tensile strength 415 N/MM² steel, TMT steel rods of TATA/ SAIL/KAMDHENU or its equivalent (C.S.I. No. 9.03 ) | Qtl. | 7.96 | 6545.2 | 52099.792
6 | Providing and fixing of Dr. fixit LW+ in RCC/CC/PLASTER etc. 200ml per bag of cement as directed by E/I including supply of all material, labour and T&P etc. required for proper completion of work.(NSI) | Ltr | 37.82 | 128.5 | 4859.87
7 | 12mm thick plaster with cement mortar consisting of one par of cement and three part of coarse sand (1:3) minimum thickness not to be less then 10mm including supply of all material, labour and T&P etc. for proper completion of work. (CSI No. 11.06) | Sqm | 304.34 | 175 | 53259.5
8 | 3 mm thick floating coat of neat cement finish including supply of all material, labour and T&P etc. required for proper completion of the work. (Cement consumtion 0.044bag/Sqm.) (CSI No. 11.20+0.044x11.15) | Sqm. | 167.89 | 23.07 | 3873.2223
9 | 1st Class brick ( class-150) work in 1:6 cement and coarse sand (F.M. 1.8.to 2.5 ). mortar in super structure including supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.6.01+6.07+6.08) | Cum. | 3.52 | 5763 | 20285.76
10 | Providing and fixing of 110 mm dia PVC Pipe 6 kg/sq.cm for with special such as Tee, bend, socket, elbow etc including supply of all labour , material T&P etc. complete required for proper completion of the work. (CSI No. 26.17) | Rm | 23.89 | 249 | 5948.61
11 | Dismantiling existing plaster including disposal of refuse as directed by the E/C with in a distance of 60M.(C.S.I.No.15.11) | Sqm | 495.5 | 32 | 15856
12 | 12mm thick plaster with cement mortar consisting of one par of cement and four part of coarse sand (1: 4) minimum thickness not to be less then 10mm including supply of all material, labour and T&P etc. for proper completion of work. (CSI No. 11.07) | Sqm | 149.11 | 158 | 23559.38
13 | 12 mm (1/2") thick plaster with cement mortar consisting of one part of cement and 6 part of coarse sand (1:6), minium thickness not to be less then 10mm including suply of all materials, labour and T&P etc. for proper completion of the work.(CSI.NO.11.09) | Sqm. | 209.94 | 148 | 31071.12
14 | Painting two coat with Acrylic/synthetic distemper of Berger/Asian over new wall interior surface over one priming coat cement primer (water based) of ICI or equivalent make as approved by E/I including supply of all materials, labour & T&P etc. required .(C.S.I.No. 13.25+13.26) | Sqm. | 209.94 | 106 | 22253.64
15 | White washing three coat including cost of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.14.03) | Sqm. | 136.45 | 14 | 1910.3
16 | Finishing of walls with water proof exterior emulsion paint of ACE of Asian paints or equialent make including 3 coats of above paint including one priming coat on already well prepared new wall surface to give an even shade including cost of all materials, labour and T&P egc. complete for proper completion of the work.(NSI) | Sqm. | 181.87 | 80 | 14549.6
17 | Dismantiling cement concrete or brick or grnolithic floors including base concrete and including stacking of dismantled materials as directed by the E/I. with in a distance 60M.(C.s.I.No.15.05) | Sqm | 138.22 | 44 | 6081.68
18 | Clearing of septic tank including disposal of waste out side the UPPCL area as per direction of the E/I. including cost of all labour T&P etc. required for proper completion of the work.(CSI No. 20.12) | N0 | 1 | 1348 | 1348
19 | 40 mm. thick C.C. 1:2:4 plain cement concrete floor with cement, approved coarse sand, and 2cm.(3/4") graded approved stone ballast laid in pannels finished with 3mm.(1/8") floating coat of neat cement or cement and marble dust in ratio of 5:1 as specified over and removing any over lapping mortar at the joints of the pannels, if any, and giving them a uniform finish including supply of all materials labour and T&P etc. required for proper completion of the work with without base concrete.(C.S.I.No.12.04) | Sqm. | 138.22 | 375 | 51832.5
20 | Providing and fixing glass strips of 3.15 mm thickness & 40mm depth in joints of floor and skriting at the time of laying floors, flush with floor level including supply of labour T&P etc. required for proper completion of the work. (C.S.I. No. 12.14) | Rm | 163.65 | 28 | 4582.2
21 | 1st Class brick ( class-150) work in 1:6 cement and coarse sand (F.M. 1.5.to 2.0 ). mortar in foundation and plinth including supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.6.01) | Cum. | 19.69 | 5205 | 102486.45
22 | Concrete with 4cm gauge stone ballast coarse sand ( F.M. 1.8 to 2.5) & cement in proportion of 12:6:1 in foundation & under floors including supply of all materials, labour and T&P etc. required for proper completion of work.(CSI No. 5.02) | Cum. | 22.16 | 4167 | 92340.72
23 | Local river sand filling in plinth including supply of necessary quantity of sand from a distances not exceeding 8 Kms. (5 miles) from the site of work including watering ramming and dressing etc. Rate include cost of all materials, labour and T & P etc. required for proper completion of the work.(C.S.I. No. 4.05) | Cum. | 20 | 587 | 11740
24 | Supply and Laying 8 mm thick glazed floor tiles of Somany, Johnson or equivalent make, of size 300x300 mm, laid with 1:3 cement and approved coarse sand mortar finished with white cement slurry, jointing and polishing complete, including supply of all materials, labour and T&P etc. completion required for proper completion of the work. (CSI No. 12.11) | Sqm | 3.89 | 1165 | 4531.85
25 | Supply and Laying 6 mm thick glazed tiles of size 200x300 mm in skirting / dado laid with 1:3 cement and approved coarse sand mortar finished with white cement slurry, jointing and polishing complete,including supply of all materials, labour and T&P etc. completion required for proper completion of the work. (CSI No. 12.12) | Sqm | 12.95 | 1000 | 12950
26 | Providing and fixing white glazed China earthen ware water closet squatting " Orisa type" pan weaper size 580mmx140mm Hindustan Make or other equivalent approved make of Ist quality with 100mm dia. White glazed P or S trap fittings including cutting & making good the walls and floors wherever required with cement sand and grit mortar not less than 1:4 the seat and trap shall have to be fixed over minimum 3" thick c.c. in proportion of 12:6:1 including cost of all materials, labour(C.S.I.No. 27.01+27.23) | Nos. | 1 | 2891 | 2891
27 | Dismantling of doors or window chowkhats including stacking of materials as directed by the E/I. within a distance of 60M.(CSI No. 15.10) | Sqm | 20.4 | 57 | 1162.8
28 | Supply and fixing of 32 mm thick single leaf flush door shutter (boiled water resistaance, phenol maldehide resin bonded, hot pressed factory made ( commercial quality to I.S. 2202 part-1 (1993) ISI marked including fixing of wooden leats and stoppers and including fixing and adjustment of hinges bolts, lokcs, handles, springs and other fitting but excluding their supply including all materials, labour & T&P etc. required for proper completion of work. ( CSI No. 8.57) | Sqm. | 6.85 | 1559 | 10679.15
29 | Mild steel or iron work in heavy sizes such as trusses built-up gates, door frames, record, racks, roof work, gates etc. wrought to required form including holes rivetting or welding where necessary and also fixing in proper position and alignment including cost of all materials supplied by contractor (CSI No. 9.01 ) | Qtl. | 11.31 | 7491.9 | 84733.389
30 | Supply and fixing galvanised mosquito proof jali ( 16x24 gauge ) with M.S. flat of 20x3mm. Size on both sides screwed or welded to window or door frame.(CSI No. 9.18) | Sqm | 10.09 | 582 | 5872.38
31 | Providing and fixing steel glazed window and ventilators of standard rolled Mann or mahavir steel section conforming to IS 7452-1974 as per drawing joints metered & welded with 100x14x3.15mm holdfast embedded in cement conctete block 15x10x10 cm. size of 1:3:6 proportion I.E. First part of cement 3 part of approved coarse sand & 6 part of graded stone (aggregated 20mm. Nominal size) S/F of glass panes of plain pin headed 4mm. Thick nuts glazing clips and special putty of approved make complete and including a cost of red oxide paint. The fabrication should conform to I.S. 1038-1975 ( Aluminum beading with rubber packing included) (CSI No. 9.17) | Sqm | 10.09 | 3828 | 38624.52
32 | Painting or varnishing new iron works or new wood work with one coat of ready mixed priming paint and two coats of approved superior quality ready mixed enamel paint 'LUXOL' or equivalent brand or varnish including supply of all materials, labour& T&P etc. required for proper completion of the work (C.S.I. No. 13.01+13.02) | Sqm. | 67.14 | 97 | 6512.58
33 | Pre-Construction anti-termite treatment, by breating a barrier under and around the coloumns pits, foundation trenches, under floors, junctions of walls & floors, around the external perimetre of building, expansion, joints, surrounding of pipes and coduits etc.(Plinth area of the building at ground floor only shall be measured as per I.S. 6313 ( Part II 1981 ) with Aldine exulsifiable 0.2% concentration or any other approved material such as Heptachlore or chlordance will be used. The consumption of emulsion shall be (i) Foundation and masonary @ 5 Ltrs /Sqm (ii) Back fills in immediate contact of foundation@ 7.5 Ltrs/Sqm ((iii) Top surface of plinth filling @ 5 Ltrs/Sqm,(iv) junction of walls & floors @ 7.5 Ltrs/Sqm (v) Soil along extermal perlimetre of building @ 7.5 Ltrs/Sqm(vi) under apron of the building @ 5 Ltrs/Sqm. The rates includes cost of all materials, labour, equipments, T&P complete.(CSI No. 17.01) | Sqm | 91.83 | 82 | 7530.06
34 | Concrete with 20mm. (1.5") gauge approved hard Stone ballast, coarse sand of ( F.M.1.5 to 2.0) and cement in proportion of 4:2:1in foundation and under floors and supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. NO. 5.06) | Cum. | 0.57 | 6386 | 3640.02
35 | Clearing jungle including uprooting of rank vegetations grass, bush, wood, trees and saplings of girth up to 30cm measured at a height of 1.0m above ground level and removal of rubbish up to a distance of 50m outside the periphery of UPPCL area cleared.(CSI No. 4.08) | Sqm | 150 | 5 | 750
36 | Providing and Fixing barbed iron wire wire fencing including stretching, fixing in to the post including all labour, materials and T&P required for proper completion of work the weight of hot dipped GI barbed wire having 12 SWG-2 ply wires and 4 point ordinary barbs @ 150mm (approx ) C/C should be 100 gm per Meter.(CSI No. 9.07) | Rmt. | 90 | 11 | 990
37 | Excavation in foundation in ordinary soil (Loam Clay or Sand) including lift upto 1.5 meter and lead upto 30 meter and including filling , watering, and ramming of excavated earth into the trenches or into the space between the building and sides of the foundation the work . (C.S.I. No 4.01) | Cum. | 7.2 | 133 | 957.6
38 | Disposal of rubbish/debris out side the UPPCL area as per direction of E/I. including cartage, labour and materials, T&P etc. required for proper completion of the work. ( No deduction for voids shall be made ) ( CSI No. 20.16). | Cum. | 25.18 | 264 | 6647.52
39 | First class brick ( Class-150) laid dry in foundation and plinth as in circular sockpit walls of one brick thickness and 2.0 to 3.0M depth including cutting moulding bricks as required including cost of all materials, labour and T&P complete (CSI No. 6.16) | Cum. | 0.8 | 4749 | 3799.2
40 | Providing and laying floor of 10mm thick industrial (heavy duty) tiles in flooring or skirting of approved brand ( Bell, Johnson or equil, make) size of 300x300mm of approved shade, clour and pattern, laid over base cement mortar 1:4 mix icluding finishing the joints with white cement mixed with pigment to match the shade of tile including cost of all material, labour and T&P required for proper completion of the work.( NSI) | Sqm | 55.24 | 1728 | 95454.72
41 | Add for extra labour and materials for plaster over rough face of one brick thick wall.(CSI No. 11.12) | Sqm | 220 | 20 | 4400
42 | Firs class bricks on edge floor laid dry joints sand filed including preparation of base to proper slope and its ramming including supply of all material labour & T&P etc. required for proper completion of the work.(CSI No. 12.07) | Sqm | 140 | 558 | 78120
43 | Providing and fixing 1mm thick M.S. sheet garrage door with frame of 40x40x6mm angle iron, diagonal bracings with 50x5 mm flat and 5mm thick M.S.gusset plates at the junctions and corner including supply and fixing of necessary fitting 2 no. lock rail of 16 dia , 375mm long and including pintel hooks at the top and bottom, applying a priming coat of red oxide paint on all sides complete. (CSI No.9.34) | Sqm | 3.2 | 3002 | 9606.4
44 | Removal of cement mortar from dismenttled bricks and stacking in countable position at place as directed by the E/I. including cost of all labour and T&P required for proper completion of work. (CSI No. 6.22) | Cum. | 6.64 | 989 | 6566.96
45 | Wiring point for light with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch & ceiling rose /single/batten holder on 3mm. thick phenolic laminated backelite sheet etc. complete in all respect, as directed including matching colour wash (PSI N0 131(C ) | Nos. | 10 | 518 | 5180
46 | Wiring point for fan /fresh air fan with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch & ceiling rose on 3mm. thick phenolic laminated backelite sheet etc. complete in all respect, as directed including matching colour wash(PSI N0.133( C) | NO | 4 | 595 | 2380
47 | Wiring point for plug with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch and socket etc.complete in all respect, including matching colour wash((PSI N0.134(C ) | NO | 5 | 275 | 1375
48 | Wiring point for exhaust fan with 1.5sq.mm FR PVC insulated multistrand single core copper conductor cable in PVCl conduit concealed in the wall, complete with 14 SWG copper earth continuity wire and 15 A piano type ceiling rose on 3mm thick phenolic laminated backelite sheet etc. complete in all respect including matching colour wash (PSI No. 137 (C ) | No. | 3 | 780 | 2340
49 | S/F of LED fluorescent tube light fitting suitable for 1x18 watt fluorescent tube complete including tubes etc. on surface complete in all respects.(NSI) | Each | 10 | 1100 | 11000
50 | Supply and fixing of high speed ceiling fan 1200mm size of USHA or any approved make by E/I. complet in all respect (NSI) | No. | 4 | 1686 | 6744
51 | S/F of MCB ( 6-32Amp) PSI 1002CAT-A | No | 8 | 250 | 2000
52 | S&F surface/flush mounting 12 ways SPN distribution board ( Legrand Lexic ) with additional metal door without MCB complete in all respect, as directed at site by E/I (PSI N0.1025A) | No | 1 | 2100 | 2100
53 | S/F of electronic fan dimmer, 120-280V , ISI marked on the existing switch board including making connnection, required material, labour T&P egc. For proper completion of work to the satisfaction of E/I. of work (PSI 1203(A) | No. | 4 | 305 | 1220
54 | Supply and fixing of power plug with 20A/250 volt flush type switch and 5 pin 20A/250V flush type universal socket in suitable M.S. box of 175mmx100mmx50mm size with phenoic laminated bakelite sheet cover 3mm thick fixed with brass machinne screw and cup washer (PSI N0.1139) (A) | No. | 4 | 595 | 2380
55 | S& F of Electrical (Porcelain) Cut Out 63Amp as directed by E/I(NSI) | No. | 4 | 300 | 1200
56 | supply and burying of 600mmx600mmx6mm GI plate vertically for earthing with its top at least 3 metres below ground tevel complete with 20mm dia g.I. pipe and funned for watering and one eahing lead of one no. 8 to 10 SWG copper wire in 15mm dia G.I.pipe up to switch board (From appron to switch board the cost of G.I. pipe and G.I. wire will be extra) 30cm square C.I. frame with hinged cover masonry housing alternate layers of charcoal/coke and salt at least 150mm thick alround etc. as per direction of E/I. complete in all respect\ (PSI N0 703) | No. | 1 | 4730 | 4730
57 | 63Amp.Double Pole Isolator (Legrand Lexic) (PSI N0 1005B) | No | 1 | 590 | 590
58 | S&F hexagonal fan box with hexagonal side of approx 80mm in length fabricated from 16 SWG MS sheet incorporating 10mm dia M.S. round bar duly bent for supporting fan hanger duly painted withred oxide and screwing arrangement with wiring conduit laid in the RCC roof before concreting along with supply of all material, labour and T&P etc. required for proper completion of the work (PSI No. 1149) | No. | 4 | 135 | 540
59 | Supply and wiring of submain with two number 4 sq.mm in PVC insulated 1100V grade multistrand single core copper conductor cable in 20 mm dia heavy duty (2mm thick)PVC conduit concealed in wall, complete with one number 2.5 sqmm. copper cable as earth continuity wire etc. complet in all respect (PSI No. 216 ( C ) | Rm | 200 | 155 | 31000
60 | Supply and wiring of submain with two number 6 sq.mm in PVC insulated 1100V grade multistrand single core copper conductor cable in 25 mm dia heavy duty (2mm thick)PVC conduit concealed in wall, complete with one number 4.00 sqmm. copper cable as earth continuity wire etc. complet in all respect (PSI No. 217( C ) | Rm | 50 | 215 | 10750
61 | supply and wiring of submain with two number 2.5 sq.mm. FR PVC insulated 1100 V grade multistrand single core copper conductor cable in 20mm dia heavy duty (2mm thick) PVC conduit with 1 number 1.5 sq.mm. FR PVCearth continuity wire complete in all respect including matching colour wash etc. complete in all respect.(PSI No. 1304C) | Rm | 200 | 121 | 24200
62 | supply and wiring of submain with two number 1.5 sq.mm. FR PVC insulated 1100 V grade multistrand single core copper conductor cable in 20mm dia heavy duty (2mm thick) PVC conduit with one number 1.5 sq.mm. FR PVC earth continuity wire complete in all respect including matching colour wash etc. complete in all respect .(PSI No. 1312C) | Rm | 50 | 104 | 5200
63 | S/F of 16 gauge M.S. drum duly painted included making hole in the wall for exhaust fan and finishing proporely complete in all respcet.(PSI No. 1122) | No. | 4 | 680 | 2720
64 | Making hole in the wall for exhaust fan and finishing properly complete in all respect (PSI N0.1121) | No. | 1 | 325 | 325
65 | Supply and fixing of factor fabricated M.S. box in existing sunk of size 600mmx480mmx200mm deep with Godrej type almirah, cover with handle etc. fabricated from 18 SWG ( 1.25mm) M.S. sheet duly painted with red oxide primer followed by two coats of synthetic enamet paint complete with necessary conduit entry and D.P. /T.P.N; fixing arrangement and provision for compartment for loose wires openable housing on the top and hold fast etc. including supply of all material., labour T&P etc. required for proper completion of the work.(PSI No. 1147) | No. | 1 | 1435 | 1435
66 | Supply and fixing of 12inch high speed exhaust fan make-USHA, havels etc or its equivalent including, labour, materials and T&P complete in all respect as directed by E/I. (NSI) | No | 3 | 1686 | 5058
67 | S/F of switch box made up to 16SWG (1.5mm) thick M.S. sheet of 100x100x65mm size duly painted with red oxide primer and flushed in wall ineluding cutting of brick work, fixing it to the level with cement sand mortar, including matching colour wash with s/o all materials, labour and T&P required for proper completion of work as directed a site by the E/I.(PSI No. 159) | No | 2 | 60 | 120
68 | Same as item no 67.but of 150x150x65mm size (PSI No.160) | No | 2 | 95 | 190
69 | Same as item no 67 .but of 175x250x65mm size (PSI No.161) | No | 2 | 90 | 180
70 | Same as item no.67 .but of 200x250x65mm size (PSI No.162) | No | 2 | 145 | 290
71 | Same as item no.67 .but of 250x250x65mm size (PSI No.163) | No | 2 | 165 | 330
72 | Construction of recess of 600mmx480mmx200mm size of main boards, distribution boards of all sizes including cutting of brick work, providing lintel of suitable size and thickness, plastering etc. with supply of all materials, labour T&P required for proper completion of work.(PSI No.1141B) | No. | 1 | 480 | 480
| Total |  |  |  | 1225653.4333
| Jr. Engr. | S.D.O |  | Ex. Engineer

## MARDAH
APPROXIMATE BILL OF QUANTITY FOR M&R OF MISC. CIVIL WORKS
AT 33/ 11 K.V. MARDAH, GHAZIPUR
Sl. | ITEM OF WORKS | UNIT | QUANTITY | RATE | AMOUNT
1 | 2 | 3 | 4 | 5 | 6
1 | Dismantiling of existing damaged Mud Faska over the roof. Cleaning the surface with wire brush, removal and disposal of rubbish at a distance 100 meters also including the cost of celaning and stacking of usable materials etc. including all labour, material required for porper completion of work.(CSI No. 15.14) | Sqm | 99.56 | 107 | 10652.92
2 | Dismantling brick work or stone work in lime or cement mortar and including stacking of materials as directied by the E/I. within a distance of 60 metres. (CSI.No.15.01) | Cum. | 2.76 | 389 | 1073.64
3 | Providing of Dr. fixit 301 pidicrete URP & mixing it properly with cement in the proportion of 1:1.5 apply two coat to the prepared surface including cost of labour, material T&P etc. as required for proper completion of work as directed by E/I.(NSI) | Sqm | 91.39 | 262 | 23944.18
4 | R.C.C. work with cement, approved coarse sand and 2 cm. (3/4") gauge approved stone ballast in the proportion of 1:1.5:3 in the SLABS excluding reinforcement and its bending but including its fixing and binding the same with 24 BWG, G.I. binding wire and including necessary centering and shuttering etc. and also including supply of all materials, labour and T&P etc. required for proper completion of the work. (Binding wire to be supplied by the contractor free of cost).(C.S.I. No. 5.24) | Cum. | 10.34 | 9117 | 94269.78
5 | Mild steel of or iron in plain work such as reinforced concrete or reinforced brick work. (when not included in over all rates) wrought to required shape as necessary including bending for proper completion of the work and including supply of steel, its wastage, bend hooks, and authorized overlapping shall be measured. Rainforcement steel of tensile strength 415 N/MM² steel, TMT steel rods of TATA/ SAIL/KAMDHENU or its equivalent (C.S.I. No. 9.03 ) | Qtl. | 8.4 | 6545.2 | 54979.68
6 | Providing and fixing of Dr. fixit LW+ in RCC/CC/PLASTER etc. 200ml per bag of cement as directed by E/I including supply of all material, labour and T&P etc. required for proper completion of work.(NSI) | Ltr | 23.23 | 128.5 | 2985.055
7 | 12mm thick plaster with cement mortar consisting of one par of cement and three part of coarse sand (1:3) minimum thickness not to be less then 10mm including supply of all material, labour and T&P etc. for proper completion of work. (CSI No. 11.06) | Sqm | 193.5 | 175 | 33862.5
8 | 3 mm thick floating coat of neat cement finish including supply of all material, labour and T&P etc. required for proper completion of the work. (Cement consumtion 0.044bag/Sqm.) (CSI No. 11.20+0.044x11.15) | Sqm. | 193.5 | 23.07 | 4464.045
9 | 1st Class brick ( class-150) work in 1:6 cement and coarse sand (F.M. 1.8.to 2.5 ). mortar in super structure including supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.6.01+6.07+6.08) | Cum. | 2.76 | 5763 | 15905.88
10 | Providing and fixing of 110 mm dia PVC Pipe 6 kg/sq.cm for with special such as Tee, bend, socket, elbow etc including supply of all labour , material T&P etc. complete required for proper completion of the work. (CSI No. 26.17) | Rm | 23 | 249 | 5727
11 | Dismantiling existing plaster including disposal of refuse as directed by the E/C with in a distance of 60M.(C.S.I.No.15.11) | Sqm | 558.5 | 32 | 17872
12 | 12mm thick plaster with cement mortar consisting of one par of cement and four part of coarse sand (1: 4) minimum thickness not to be less then 10mm including supply of all material, labour and T&P etc. for proper completion of work. (CSI No. 11.07) | Sqm | 236.7 | 158 | 37398.6
13 | 12 mm (1/2") thick plaster with cement mortar consisting of one part of cement and 6 part of coarse sand (1:6), minium thickness not to be less then 10mm including suply of all materials, labour and T&P etc. for proper completion of the work.(CSI.NO.11.09) | Sqm. | 240.24 | 148 | 35555.52
14 | Painting two coat with Acrylic/synthetic distemper of Berger/Asian over new wall interior surface over one priming coat cement primer (water based) of ICI or equivalent make as approved by E/I including supply of all materials, labour & T&P etc. required .(C.S.I.No. 13.25+13.26) | Sqm. | 240.24 | 106 | 25465.44
15 | White washing three coat including cost of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.14.03) | Sqm. | 91 | 14 | 1274
16 | Finishing of walls with water proof exterior emulsion paint of ACE of Asian paints or equialent make including 3 coats of above paint including one priming coat on already well prepared new wall surface to give an even shade including cost of all materials, labour and T&P egc. complete for proper completion of the work.(NSI) | Sqm. | 246.7 | 80 | 19736
17 | Dismantiling cement concrete or brick or grnolithic floors including base concrete and including stacking of dismantled materials as directed by the E/I. with in a distance 60M.(C.s.I.No.15.05) | Sqm | 103.73 | 44 | 4564.12
18 | Clearing of septic tank including disposal of waste out side the UPPCL area as per direction of the E/I. including cost of all labour T&P etc. required for proper completion of the work.(CSI No. 20.12) | N0 | 1 | 1348 | 1348
19 | 40 mm. thick C.C. 1:2:4 plain cement concrete floor with cement, approved coarse sand, and 2cm.(3/4") graded approved stone ballast laid in pannels finished with 3mm.(1/8") floating coat of neat cement or cement and marble dust in ratio of 5:1 as specified over and removing any over lapping mortar at the joints of the pannels, if any, and giving them a uniform finish including supply of all materials labour and T&P etc. required for proper completion of the work with without base concrete.(C.S.I.No.12.04) | Sqm. | 103.73 | 375 | 38898.75
20 | Providing and fixing glass strips of 3.15 mm thickness & 40mm depth in joints of floor and skriting at the time of laying floors, flush with floor level including supply of labour T&P etc. required for proper completion of the work. (C.S.I. No. 12.14) | Rm | 309.43 | 28 | 8664.04
21 | 1st Class brick ( class-150) work in 1:6 cement and coarse sand (F.M. 1.5.to 2.0 ). mortar in foundation and plinth including supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.6.01) | Cum. | 9.84 | 5205 | 51217.2
22 | Concrete with 4cm gauge stone ballast coarse sand ( F.M. 1.8 to 2.5) & cement in proportion of 12:6:1 in foundation & under floors including supply of all materials, labour and T&P etc. required for proper completion of work.(CSI No. 5.02) | Cum. | 30 | 4167 | 125010
23 | Local river sand filling in plinth including supply of necessary quantity of sand from a distances not exceeding 8 Kms. (5 miles) from the site of work including watering ramming and dressing etc. Rate include cost of all materials, labour and T & P etc. required for proper completion of the work.(C.S.I. No. 4.05) | Cum. | 60 | 587 | 35220
24 | Supply and Laying 8 mm thick glazed floor tiles of Somany, Johnson or equivalent make, of size 300x300 mm, laid with 1:3 cement and approved coarse sand mortar finished with white cement slurry, jointing and polishing complete, including supply of all materials, labour and T&P etc. completion required for proper completion of the work. (CSI No. 12.11) | Sqm | 3.53 | 1165 | 4112.45
25 | Supply and Laying 6 mm thick glazed tiles of size 200x300 mm in skirting / dado laid with 1:3 cement and approved coarse sand mortar finished with white cement slurry, jointing and polishing complete,including supply of all materials, labour and T&P etc. completion required for proper completion of the work. (CSI No. 12.12) | Sqm | 12.37 | 1000 | 12370
26 | Providing and fixing white glazed China earthen ware water closet squatting " Orisa type" pan weaper size 580mmx140mm Hindustan Make or other equivalent approved make of Ist quality with 100mm dia. White glazed P or S trap fittings including cutting & making good the walls and floors wherever required with cement sand and grit mortar not less than 1:4 the seat and trap shall have to be fixed over minimum 3" thick c.c. in proportion of 12:6:1 including cost of all materials, labour(C.S.I.No. 27.01+27.23) | Nos. | 1 | 2891 | 2891
27 | Dismantling of doors or window chowkhats including stacking of materials as directed by the E/I. within a distance of 60M.(CSI No. 15.10) | Sqm | 19.69 | 57 | 1122.33
28 | Supply and fixing of 32 mm thick single leaf flush door shutter (boiled water resistaance, phenol maldehide resin bonded, hot pressed factory made ( commercial quality to I.S. 2202 part-1 (1993) ISI marked including fixing of wooden leats and stoppers and including fixing and adjustment of hinges bolts, lokcs, handles, springs and other fitting but excluding their supply including all materials, labour & T&P etc. required for proper completion of work. ( CSI No. 8.57) | Sqm. | 6.64 | 1559 | 10351.76
29 | Mild steel or iron work in heavy sizes such as trusses built-up gates, door frames, record, racks, roof work, gates etc. wrought to required form including holes rivetting or welding where necessary and also fixing in proper position and alignment including cost of all materials supplied by contractor (CSI No. 9.01 ) | Qtl. | 10.23 | 7491.9 | 76642.137
30 | Supply and fixing galvanised mosquito proof jali ( 16x24 gauge ) with M.S. flat of 20x3mm. Size on both sides screwed or welded to window or door frame.(CSI No. 9.18) | Sqm | 9.63 | 582 | 5604.66
31 | Providing and fixing steel glazed window and ventilators of standard rolled Mann or mahavir steel section conforming to IS 7452-1974 as per drawing joints metered & welded with 100x14x3.15mm holdfast embedded in cement conctete block 15x10x10 cm. size of 1:3:6 proportion I.E. First part of cement 3 part of approved coarse sand & 6 part of graded stone (aggregated 20mm. Nominal size) S/F of glass panes of plain pin headed 4mm. Thick nuts glazing clips and special putty of approved make complete and including a cost of red oxide paint. The fabrication should conform to I.S. 1038-1975 ( Aluminum beading with rubber packing included) (CSI No. 9.17) | Sqm | 9.63 | 3828 | 36863.64
32 | Painting or varnishing new iron works or new wood work with one coat of ready mixed priming paint and two coats of approved superior quality ready mixed enamel paint 'LUXOL' or equivalent brand or varnish including supply of all materials, labour& T&P etc. required for proper completion of the work (C.S.I. No. 13.01+13.02) | Sqm. | 48.84 | 97 | 4737.48
33 | Pre-Construction anti-termite treatment, by breating a barrier under and around the coloumns pits, foundation trenches, under floors, junctions of walls & floors, around the external perimetre of building, expansion, joints, surrounding of pipes and coduits etc.(Plinth area of the building at ground floor only shall be measured as per I.S. 6313 ( Part II 1981 ) with Aldine exulsifiable 0.2% concentration or any other approved material such as Heptachlore or chlordance will be used. The consumption of emulsion shall be (i) Foundation and masonary @ 5 Ltrs /Sqm (ii) Back fills in immediate contact of foundation@ 7.5 Ltrs/Sqm ((iii) Top surface of plinth filling @ 5 Ltrs/Sqm,(iv) junction of walls & floors @ 7.5 Ltrs/Sqm (v) Soil along extermal perlimetre of building @ 7.5 Ltrs/Sqm(vi) under apron of the building @ 5 Ltrs/Sqm. The rates includes cost of all materials, labour, equipments, T&P complete.(CSI No. 17.01) | Sqm | 91.83 | 82 | 7530.06
34 | Concrete with 20mm. (1.5") gauge approved hard Stone ballast, coarse sand of ( F.M.1.5 to 2.0) and cement in proportion of 4:2:1in foundation and under floors and supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. NO. 5.06) | Cum. | 0.57 | 6386 | 3640.02
35 | Clearing jungle including uprooting of rank vegetations grass, bush, wood, trees and saplings of girth up to 30cm measured at a height of 1.0m above ground level and removal of rubbish up to a distance of 50m outside the periphery of UPPCL area cleared.(CSI No. 4.08) | Sqm | 150 | 5 | 750
36 | Providing and Fixing barbed iron wire wire fencing including stretching, fixing in to the post including all labour, materials and T&P required for proper completion of work the weight of hot dipped GI barbed wire having 12 SWG-2 ply wires and 4 point ordinary barbs @ 150mm (approx ) C/C should be 100 gm per Meter.(CSI No. 9.07) | Rmt. | 90 | 11 | 990
37 | Excavation in foundation in ordinary soil (Loam Clay or Sand) including lift upto 1.5 meter and lead upto 30 meter and including filling , watering, and ramming of excavated earth into the trenches or into the space between the building and sides of the foundation the work . (C.S.I. No 4.01) | Cum. | 7.2 | 133 | 957.6
38 | Disposal of rubbish/debris out side the UPPCL area as per direction of E/I. including cartage, labour and materials, T&P etc. required for proper completion of the work. ( No deduction for voids shall be made ) ( CSI No. 20.16). | Cum. | 15.4 | 264 | 4065.6
39 | First class brick ( Class-150) laid dry in foundation and plinth as in circular sockpit walls of one brick thickness and 2.0 to 3.0M depth including cutting moulding bricks as required including cost of all materials, labour and T&P complete (CSI No. 6.16) | Cum. | 0.8 | 4749 | 3799.2
40 | Providing and laying floor of 10mm thick industrial (heavy duty) tiles in flooring or skirting of approved brand ( Bell, Johnson or equil, make) size of 300x300mm of approved shade, clour and pattern, laid over base cement mortar 1:4 mix icluding finishing the joints with white cement mixed with pigment to match the shade of tile including cost of all material, labour and T&P required for proper completion of the work.( NSI) | Sqm | 56 | 1728 | 96768
41 | Add for extra labour and materials for plaster over rough face of one brick thick wall.(CSI No. 11.12) | Sqm | 220 | 20 | 4400
42 | Firs class bricks on edge floor laid dry joints sand filed including preparation of base to proper slope and its ramming including supply of all material labour & T&P etc. required for proper completion of the work.(CSI No. 12.07) | Sqm | 186.8 | 558 | 104234.4
43 | Providing and fixing 1mm thick M.S. sheet garrage door with frame of 40x40x6mm angle iron, diagonal bracings with 50x5 mm flat and 5mm thick M.S.gusset plates at the junctions and corner including supply and fixing of necessary fitting 2 no. lock rail of 16 dia , 375mm long and including pintel hooks at the top and bottom, applying a priming coat of red oxide paint on all sides complete. (CSI No.9.34) | Sqm | 3.2 | 3002 | 9606.4
44 | Removal of cement mortar from dismenttled bricks and stacking in countable position at place as directed by the E/I. including cost of all labour and T&P required for proper completion of work. (CSI No. 6.22) | Cum. | 6.64 | 989 | 6566.96
46 | Wiring point for light with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch & ceiling rose /single/batten holder on 3mm. thick phenolic laminated backelite sheet etc. complete in all respect, as directed including matching colour wash (PSI N0 131(C ) | Nos. | 10 | 518 | 5180
47 | Wiring point for fan /fresh air fan with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch & ceiling rose on 3mm. thick phenolic laminated backelite sheet etc. complete in all respect, as directed including matching colour wash(PSI N0.133( C) | NO | 4 | 595 | 2380
48 | Wiring point for plug with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch and socket etc.complete in all respect, including matching colour wash((PSI N0.134(C ) | NO | 5 | 275 | 1375
49 | Wiring point for exhaust fan with 1.5sq.mm FR PVC insulated multistrand single core copper conductor cable in PVCl conduit concealed in the wall, complete with 14 SWG copper earth continuity wire and 15 A piano type ceiling rose on 3mm thick phenolic laminated backelite sheet etc. complete in all respect including matching colour wash (PSI No. 137 (C ) | No. | 3 | 780 | 2340
50 | S/F of LED fluorescent tube light fitting suitable for 1x18 watt fluorescent tube complete including tubes etc. on surface complete in all respects.(NSI) | Each | 10 | 1100 | 11000
51 | Supply and fixing of high speed ceiling fan 1200mm size of USHA or any approved make by E/I. complet in all respect (NSI) | No. | 4 | 1686 | 6744
52 | S/F of MCB ( 6-32Amp) PSI 1002CAT-A | No | 8 | 250 | 2000
53 | S&F surface/flush mounting 12 ways SPN distribution board ( Legrand Lexic ) with additional metal door without MCB complete in all respect, as directed at site by E/I (PSI N0.1025A) CAT-A | No | 1 | 2100 | 2100
54 | S/F of electronic fan dimmer, 120-280V , ISI marked on the existing switch board including making connnection, required material, labour T&P egc. For proper completion of work to the satisfaction of E/I. of work (PSI 1203(A) | No. | 4 | 305 | 1220
55 | Supply and fixing of power plug with 20A/250 volt flush type switch and 5 pin 20A/250V flush type universal socket in suitable M.S. box of 175mmx100mmx50mm size with phenoic laminated bakelite sheet cover 3mm thick fixed with brass machinne screw and cup washer (PSI N0.1139) (A) | No. | 4 | 595 | 2380
56 | S& F of Electrical (Porcelain) Cut Out 63Amp as directed by E/I(NSI) | No. | 4 | 300 | 1200
57 | supply and burying of 600mmx600mmx6mm GI plate vertically for earthing with its top at least 3 metres below ground tevel complete with 20mm dia g.I. pipe and funned for watering and one eahing lead of one no. 8 to 10 SWG copper wire in 15mm dia G.I.pipe up to switch board (From appron to switch board the cost of G.I. pipe and G.I. wire will be extra) 30cm square C.I. frame with hinged cover masonry housing alternate layers of charcoal/coke and salt at least 150mm thick alround etc. as per direction of E/I. complete in all respect\ (PSI N0 703) | No. | 1 | 4730 | 4730
58 | 63Amp.Double Pole Isolator (Legrand Lexic) (PSI N0 1005B) CAT-A | No | 1 | 590 | 590
59 | S&F hexagonal fan box with hexagonal side of approx 80mm in length fabricated from 16 SWG MS sheet incorporating 10mm dia M.S. round bar duly bent for supporting fan hanger duly painted withred oxide and screwing arrangement with wiring conduit laid in the RCC roof before concreting along with supply of all material, labour and T&P etc. required for proper completion of the work (PSI No. 1149) | No. | 4 | 135 | 540
60 | Supply and wiring of submain with two number 4 sq.mm in PVC insulated 1100V grade multistrand single core copper conductor cable in 20 mm dia heavy duty (2mm thick)PVC conduit concealed in wall, complete with one number 2.5 sqmm. copper cable as earth continuity wire etc. complet in all respect (PSI No. 216 ( C ) | Rm | 200 | 155 | 31000
61 | Supply and wiring of submain with two number 6 sq.mm in PVC insulated 1100V grade multistrand single core copper conductor cable in 25 mm dia heavy duty (2mm thick)PVC conduit concealed in wall, complete with one number 4.00 sqmm. copper cable as earth continuity wire etc. complet in all respect (PSI No. 217( C ) | Rm | 50 | 215 | 10750
62 | supply and wiring of submain with two number 2.5 sq.mm. FR PVC insulated 1100 V grade multistrand single core copper conductor cable in 20mm dia heavy duty (2mm thick) PVC conduit with 1 number 1.5 sq.mm. FR PVCearth continuity wire complete in all respect including matching colour wash etc. complete in all respect.(PSI No. 1304C) | Rm | 200 | 121 | 24200
63 | supply and wiring of submain with two number 1.5 sq.mm. FR PVC insulated 1100 V grade multistrand single core copper conductor cable in 20mm dia heavy duty (2mm thick) PVC conduit with one number 1.5 sq.mm. FR PVC earth continuity wire complete in all respect including matching colour wash etc. complete in all respect .(PSI No. 1312C) | Rm | 50 | 104 | 5200
64 | S/F of 16 gauge M.S. drum duly painted included making hole in the wall for exhaust fan and finishing proporely complete in all respcet.(PSI No. 1122) | No. | 4 | 680 | 2720
65 | Making hole in the wall for exhaust fan and finishing properly complete in all respect (PSI N0.1121) | No. | 1 | 325 | 325
66 | Supply and fixing of factor fabricated M.S. box in existing sunk of size 600mmx480mmx200mm deep with Godrej type almirah, cover with handle etc. fabricated from 18 SWG ( 1.25mm) M.S. sheet duly painted with red oxide primer followed by two coats of synthetic enamet paint complete with necessary conduit entry and D.P. /T.P.N; fixing arrangement and provision for compartment for loose wires openable housing on the top and hold fast etc. including supply of all material., labour T&P etc. required for proper completion of the work.(PSI No. 1147) | No. | 1 | 1435 | 1435
67 | Supply and fixing of 12inch high speed exhaust fan make-USHA, havels etc or its equivalent including, labour, materials and T&P complete in all respect as directed by E/I. (NSI) | No | 3 | 1686 | 5058
68 | S/F of switch box made up to 16SWG (1.5mm) thick M.S. sheet of 100x100x65mm size duly painted with red oxide primer and flushed in wall ineluding cutting of brick work, fixing it to the level with cement sand mortar, including matching colour wash with s/o all materials, labour and T&P required for proper completion of work as directed a site by the E/I.(PSI No. 159) | No | 2 | 60 | 120
69 | Same as item no 68.but of 150x150x65mm size (PSI No.160) | No | 2 | 95 | 190
70 | Same as item no 68 .but of 175x250x65mm size (PSI No.161) | No | 2 | 90 | 180
71 | Same as item no.68 .but of 200x250x65mm size (PSI No.162) | No | 2 | 145 | 290
72 | Same as item no.68 .but of 250x250x65mm size (PSI No.163) | No | 2 | 165 | 330
73 | Construction of recess of 600mmx480mmx200mm size of main boards, distribution boards of all sizes including cutting of brick work, providing lintel of suitable size and thickness, plastering etc. with supply of all materials, labour T&P required for proper completion of work.(PSI No.1141B) | No. | 1 | 480 | 480
| Total |  |  |  | 1174149.047
| Jr. Engr. | S.D.O |  | Ex. Engineer

## BAHADOORGANJ
APPROXIMATE BILL OF QUANTITY FOR M&R OF MISC. CIVIL WORKS
AT 33/ 11 K.V. BAHADURGANJ, GHAZIPUR
Sl. | ITEM OF WORKS | UNIT | QUANTITY | RATE | AMOUNT
1 | 2 | 3 | 4 | 5 | 6
1 | Dismantiling of existing damaged Mud Faska over the roof. Cleaning the surface with wire brush, removal and disposal of rubbish at a distance 100 meters also including the cost of celaning and stacking of usable materials etc. including all labour, material required for porper completion of work.(CSI No. 15.14) | Sqm | 160.54 | 107 | 17177.78
2 | Dismantling brick work or stone work in lime or cement mortar and including stacking of materials as directied by the E/I. within a distance of 60 metres. (CSI.No.15.01) | Cum. | 3.71 | 389 | 1443.19
3 | Providing of Dr. fixit 301 pidicrete URP & mixing it properly with cement in the proportion of 1:1.5 apply two coat to the prepared surface including cost of labour, material T&P etc. as required for proper completion of work as directed by E/I.(NSI) | Sqm | 159.28 | 262 | 41731.36
4 | R.C.C. work with cement, approved coarse sand and 2 cm. (3/4") gauge approved stone ballast in the proportion of 1:1.5:3 in the SLABS excluding reinforcement and its bending but including its fixing and binding the same with 24 BWG, G.I. binding wire and including necessary centering and shuttering etc. and also including supply of all materials, labour and T&P etc. required for proper completion of the work. (Binding wire to be supplied by the contractor free of cost).(C.S.I. No. 5.24) | Cum. | 6.21 | 9117 | 56616.57
5 | Mild steel of or iron in plain work such as reinforced concrete or reinforced brick work. (when not included in over all rates) wrought to required shape as necessary including bending for proper completion of the work and including supply of steel, its wastage, bend hooks, and authorized overlapping shall be measured. Rainforcement steel of tensile strength 415 N/MM² steel, TMT steel rods of TATA/ SAIL/KAMDHENU or its equivalent (C.S.I. No. 9.03 ) | Qtl. | 2.89 | 6545.2 | 18915.628
6 | Providing and fixing of Dr. fixit LW+ in RCC/CC/PLASTER etc. 200ml per bag of cement as directed by E/I including supply of all material, labour and T&P etc. required for proper completion of work.(NSI) | Ltr | 14.87 | 128.5 | 1910.795
7 | 12mm thick plaster with cement mortar consisting of one par of cement and three part of coarse sand (1:3) minimum thickness not to be less then 10mm including supply of all material, labour and T&P etc. for proper completion of work. (CSI No. 11.06) | Sqm | 378.56 | 175 | 66248
8 | 3 mm thick floating coat of neat cement finish including supply of all material, labour and T&P etc. required for proper completion of the work. (Cement consumtion 0.044bag/Sqm.) (CSI No. 11.20+0.044x11.15) | Sqm. | 159.28 | 23.07 | 3674.5896
9 | 1st Class brick ( class-150) work in 1:6 cement and coarse sand (F.M. 1.8.to 2.5 ). mortar in super structure including supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.6.01+6.07+6.08) | Cum. | 2.94 | 5763 | 16943.22
10 | Providing and fixing of 110 mm dia PVC Pipe 6 kg/sq.cm for with special such as Tee, bend, socket, elbow etc including supply of all labour , material T&P etc. complete required for proper completion of the work. (CSI No. 26.17) | Rm | 23.03 | 249 | 5734.47
11 | Dismantiling existing plaster including disposal of refuse as directed by the E/C with in a distance of 60M.(C.S.I.No.15.11) | Sqm | 545.03 | 32 | 17440.96
12 | 12mm thick plaster with cement mortar consisting of one par of cement and four part of coarse sand (1: 4) minimum thickness not to be less then 10mm including supply of all material, labour and T&P etc. for proper completion of work. (CSI No. 11.07) | Sqm | 161.73 | 158 | 25553.34
13 | 12 mm (1/2") thick plaster with cement mortar consisting of one part of cement and 6 part of coarse sand (1:6), minium thickness not to be less then 10mm including suply of all materials, labour and T&P etc. for proper completion of the work.(CSI.NO.11.09) | Sqm. | 228.07 | 148 | 33754.36
14 | Painting two coat with Acrylic/synthetic distemper of Berger/Asian over new wall interior surface over one priming coat cement primer (water based) of ICI or equivalent make as approved by E/I including supply of all materials, labour & T&P etc. required .(C.S.I.No. 13.25+13.26) | Sqm. | 228.07 | 106 | 24175.42
15 | White washing three coat including cost of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.14.03) | Sqm. | 159.28 | 14 | 2229.92
16 | Finishing of walls with water proof exterior emulsion paint of ACE of Asian paints or equialent make including 3 coats of above paint including one priming coat on already well prepared new wall surface to give an even shade including cost of all materials, labour and T&P egc. complete for proper completion of the work.(NSI) | Sqm. | 201.8 | 80 | 16144
17 | Dismantiling cement concrete or brick or grnolithic floors including base concrete and including stacking of dismantled materials as directed by the E/I. with in a distance 60M.(C.s.I.No.15.05) | Sqm | 129.69 | 44 | 5706.36
18 | Clearing of septic tank including disposal of waste out side the UPPCL area as per direction of the E/I. including cost of all labour T&P etc. required for proper completion of the work.(CSI No. 20.12) | N0 | 1 | 1348 | 1348
19 | 40 mm. thick C.C. 1:2:4 plain cement concrete floor with cement, approved coarse sand, and 2cm.(3/4") graded approved stone ballast laid in pannels finished with 3mm.(1/8") floating coat of neat cement or cement and marble dust in ratio of 5:1 as specified over and removing any over lapping mortar at the joints of the pannels, if any, and giving them a uniform finish including supply of all materials labour and T&P etc. required for proper completion of the work with without base concrete.(C.S.I.No.12.04) | Sqm. | 79.23 | 375 | 29711.25
20 | Providing and fixing glass strips of 3.15 mm thickness & 40mm depth in joints of floor and skriting at the time of laying floors, flush with floor level including supply of labour T&P etc. required for proper completion of the work. (C.S.I. No. 12.14) | Rm | 158.67 | 28 | 4442.76
21 | 1st Class brick ( class-150) work in 1:6 cement and coarse sand (F.M. 1.5.to 2.0 ). mortar in foundation and plinth including supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.6.01) | Cum. | 7.63 | 5205 | 39714.15
22 | Concrete with 4cm gauge stone ballast coarse sand ( F.M. 1.8 to 2.5) & cement in proportion of 12:6:1 in foundation & under floors including supply of all materials, labour and T&P etc. required for proper completion of work.(CSI No. 5.02) | Cum. | 9.63 | 4167 | 40128.21
23 | Local river sand filling in plinth including supply of necessary quantity of sand from a distances not exceeding 8 Kms. (5 miles) from the site of work including watering ramming and dressing etc. Rate include cost of all materials, labour and T & P etc. required for proper completion of the work.(C.S.I. No. 4.05) | Cum. | 8.2 | 587 | 4813.4
24 | Supply and Laying 8 mm thick glazed floor tiles of Somany, Johnson or equivalent make, of size 300x300 mm, laid with 1:3 cement and approved coarse sand mortar finished with white cement slurry, jointing and polishing complete, including supply of all materials, labour and T&P etc. completion required for proper completion of the work. (CSI No. 12.11) | Sqm | 3.194 | 1165 | 3721.01
25 | Supply and Laying 6 mm thick glazed tiles of size 200x300 mm in skirting / dado laid with 1:3 cement and approved coarse sand mortar finished with white cement slurry, jointing and polishing complete,including supply of all materials, labour and T&P etc. completion required for proper completion of the work. (CSI No. 12.12) | Sqm | 14.3 | 1000 | 14300
26 | Providing and fixing white glazed China earthen ware water closet squatting " Orisa type" pan weaper size 580mmx140mm Hindustan Make or other equivalent approved make of Ist quality with 100mm dia. White glazed P or S trap fittings including cutting & making good the walls and floors wherever required with cement sand and grit mortar not less than 1:4 the seat and trap shall have to be fixed over minimum 3" thick c.c. in proportion of 12:6:1 including cost of all materials, labour(C.S.I.No. 27.01+27.23) | Nos. | 1 | 2891 | 2891
27 | Dismantling of doors or window chowkhats including stacking of materials as directed by the E/I. within a distance of 60M.(CSI No. 15.10) | Sqm | 19.79 | 57 | 1128.03
28 | Supply and fixing of 32 mm thick single leaf flush door shutter (boiled water resistaance, phenol maldehide resin bonded, hot pressed factory made ( commercial quality to I.S. 2202 part-1 (1993) ISI marked including fixing of wooden leats and stoppers and including fixing and adjustment of hinges bolts, lokcs, handles, springs and other fitting but excluding their supply including all materials, labour & T&P etc. required for proper completion of work. ( CSI No. 8.57) | Sqm. | 6.7 | 1559 | 10445.3
29 | Mild steel or iron work in heavy sizes such as trusses built-up gates, door frames, record, racks, roof work, gates etc. wrought to required form including holes rivetting or welding where necessary and also fixing in proper position and alignment including cost of all materials supplied by contractor (CSI No. 9.01 ) | Qtl. | 2.98 | 7491.9 | 22325.862
30 | Supply and fixing galvanised mosquito proof jali ( 16x24 gauge ) with M.S. flat of 20x3mm. Size on both sides screwed or welded to window or door frame.(CSI No. 9.18) | Sqm | 9.63 | 582 | 5604.66
31 | Providing and fixing steel glazed window and ventilators of standard rolled Mann or mahavir steel section conforming to IS 7452-1974 as per drawing joints metered & welded with 100x14x3.15mm holdfast embedded in cement conctete block 15x10x10 cm. size of 1:3:6 proportion I.E. First part of cement 3 part of approved coarse sand & 6 part of graded stone (aggregated 20mm. Nominal size) S/F of glass panes of plain pin headed 4mm. Thick nuts glazing clips and special putty of approved make complete and including a cost of red oxide paint. The fabrication should conform to I.S. 1038-1975 ( Aluminum beading with rubber packing included) (CSI No. 9.17) | Sqm | 9.63 | 3828 | 36863.64
32 | Painting or varnishing new iron works or new wood work with one coat of ready mixed priming paint and two coats of approved superior quality ready mixed enamel paint 'LUXOL' or equivalent brand or varnish including supply of all materials, labour& T&P etc. required for proper completion of the work (C.S.I. No. 13.01+13.02) | Sqm. | 37.36 | 97 | 3623.92
33 | Pre-Construction anti-termite treatment, by breating a barrier under and around the coloumns pits, foundation trenches, under floors, junctions of walls & floors, around the external perimetre of building, expansion, joints, surrounding of pipes and coduits etc.(Plinth area of the building at ground floor only shall be measured as per I.S. 6313 ( Part II 1981 ) with Aldine exulsifiable 0.2% concentration or any other approved material such as Heptachlore or chlordance will be used. The consumption of emulsion shall be (i) Foundation and masonary @ 5 Ltrs /Sqm (ii) Back fills in immediate contact of foundation@ 7.5 Ltrs/Sqm ((iii) Top surface of plinth filling @ 5 Ltrs/Sqm,(iv) junction of walls & floors @ 7.5 Ltrs/Sqm (v) Soil along extermal perlimetre of building @ 7.5 Ltrs/Sqm(vi) under apron of the building @ 5 Ltrs/Sqm. The rates includes cost of all materials, labour, equipments, T&P complete.(CSI No. 17.01) | Sqm | 91.83 | 82 | 7530.06
34 | Concrete with 20mm. (1.5") gauge approved hard Stone ballast, coarse sand of ( F.M.1.5 to 2.0) and cement in proportion of 4:2:1in foundation and under floors and supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. NO. 5.06) | Cum. | 0.57 | 6386 | 3640.02
35 | Clearing jungle including uprooting of rank vegetations grass, bush, wood, trees and saplings of girth up to 30cm measured at a height of 1.0m above ground level and removal of rubbish up to a distance of 50m outside the periphery of UPPCL area cleared.(CSI No. 4.08) | Sqm | 150 | 5 | 750
36 | Providing and Fixing barbed iron wire wire fencing including stretching, fixing in to the post including all labour, materials and T&P required for proper completion of work the weight of hot dipped GI barbed wire having 12 SWG-2 ply wires and 4 point ordinary barbs @ 150mm (approx ) C/C should be 100 gm per Meter.(CSI No. 9.07) | Rmt. | 90 | 11 | 990
37 | Excavation in foundation in ordinary soil (Loam Clay or Sand) including lift upto 1.5 meter and lead upto 30 meter and including filling , watering, and ramming of excavated earth into the trenches or into the space between the building and sides of the foundation the work . (C.S.I. No 4.01) | Cum. | 2.5 | 133 | 332.5
38 | Disposal of rubbish/debris out side the UPPCL area as per direction of E/I. including cartage, labour and materials, T&P etc. required for proper completion of the work. ( No deduction for voids shall be made ) ( CSI No. 20.16). | Cum. | 24.38 | 264 | 6436.32
39 | First class brick ( Class-150) laid dry in foundation and plinth as in circular sockpit walls of one brick thickness and 2.0 to 3.0M depth including cutting moulding bricks as required including cost of all materials, labour and T&P complete (CSI No. 6.16) | Cum. | 0.8 | 4749 | 3799.2
40 | Providing and laying floor of 10mm thick industrial (heavy duty) tiles in flooring or skirting of approved brand ( Bell, Johnson or equil, make) size of 300x300mm of approved shade, clour and pattern, laid over base cement mortar 1:4 mix icluding finishing the joints with white cement mixed with pigment to match the shade of tile including cost of all material, labour and T&P required for proper completion of the work.( NSI) | Sqm | 50.24 | 1728 | 86814.72
41 | Add for extra labour and materials for plaster over rough face of one brick thick wall.(CSI No. 11.12) | Sqm | 220 | 20 | 4400
42 | Firs class bricks on edge floor laid dry joints sand filed including preparation of base to proper slope and its ramming including supply of all material labour & T&P etc. required for proper completion of the work.(CSI No. 12.07) | Sqm | 20 | 558 | 11160
43 | Providing and fixing 1mm thick M.S. sheet garrage door with frame of 40x40x6mm angle iron, diagonal bracings with 50x5 mm flat and 5mm thick M.S.gusset plates at the junctions and corner including supply and fixing of necessary fitting 2 no. lock rail of 16 dia , 375mm long and including pintel hooks at the top and bottom, applying a priming coat of red oxide paint on all sides complete. (CSI No.9.34) | Sqm | 3.2 | 3002 | 9606.4
44 | Removal of cement mortar from dismenttled bricks and stacking in countable position at place as directed by the E/I. including cost of all labour and T&P required for proper completion of work. (CSI No. 6.22) | Cum. | 6.64 | 989 | 6566.96
45 | Wiring point for light with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch & ceiling rose /single/batten holder on 3mm. thick phenolic laminated backelite sheet etc. complete in all respect, as directed including matching colour wash (PSI N0 131(C ) | Nos. | 10 | 518 | 5180
46 | Wiring point for fan /fresh air fan with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch & ceiling rose on 3mm. thick phenolic laminated backelite sheet etc. complete in all respect, as directed including matching colour wash(PSI N0.133( C) | NO | 4 | 595 | 2380
47 | Wiring point for plug with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch and socket etc.complete in all respect, including matching colour wash((PSI N0.134(C ) | NO | 5 | 275 | 1375
48 | Wiring point for exhaust fan with 1.5sq.mm FR PVC insulated multistrand single core copper conductor cable in PVCl conduit concealed in the wall, complete with 14 SWG copper earth continuity wire and 15 A piano type ceiling rose on 3mm thick phenolic laminated backelite sheet etc. complete in all respect including matching colour wash (PSI No. 137 (C ) | No. | 3 | 780 | 2340
49 | S/F of LED fluorescent tube light fitting suitable for 1x18 watt fluorescent tube complete including tubes etc. on surface complete in all respects.(NSI) | Each | 10 | 1100 | 11000
50 | Supply and fixing of high speed ceiling fan 1200mm size of USHA or any approved make by E/I. complet in all respect (NSI) | No. | 4 | 1686 | 6744
51 | S/F of MCB ( 6-32Amp) PSI 1002CAT-A | No | 8 | 250 | 2000
52 | S&F surface/flush mounting 12 ways SPN distribution board ( Legrand Lexic ) with additional metal door without MCB complete in all respect, as directed at site by E/I (PSI N0.1025A) CAT-A | No | 1 | 2100 | 2100
53 | S/F of electronic fan dimmer, 120-280V , ISI marked on the existing switch board including making connnection, required material, labour T&P egc. For proper completion of work to the satisfaction of E/I. of work (PSI 1203(A) | No. | 4 | 305 | 1220
54 | Supply and fixing of power plug with 20A/250 volt flush type switch and 5 pin 20A/250V flush type universal socket in suitable M.S. box of 175mmx100mmx50mm size with phenoic laminated bakelite sheet cover 3mm thick fixed with brass machinne screw and cup washer (PSI N0.1139) (A) | No. | 4 | 595 | 2380
55 | S& F of Electrical (Porcelain) Cut Out 63Amp as directed by E/I(NSI) | No. | 4 | 300 | 1200
56 | supply and burying of 600mmx600mmx6mm GI plate vertically for earthing with its top at least 3 metres below ground tevel complete with 20mm dia g.I. pipe and funned for watering and one eahing lead of one no. 8 to 10 SWG copper wire in 15mm dia G.I.pipe up to switch board (From appron to switch board the cost of G.I. pipe and G.I. wire will be extra) 30cm square C.I. frame with hinged cover masonry housing alternate layers of charcoal/coke and salt at least 150mm thick alround etc. as per direction of E/I. complete in all respect\ (PSI N0 703) | No. | 1 | 4730 | 4730
57 | 63Amp.Double Pole Isolator (Legrand Lexic) (PSI N0 1005B) | No | 1 | 590 | 590
58 | S&F hexagonal fan box with hexagonal side of approx 80mm in length fabricated from 16 SWG MS sheet incorporating 10mm dia M.S. round bar duly bent for supporting fan hanger duly painted withred oxide and screwing arrangement with wiring conduit laid in the RCC roof before concreting along with supply of all material, labour and T&P etc. required for proper completion of the work (PSI No. 1149) | No. | 4 | 135 | 540
59 | Supply and wiring of submain with two number 4 sq.mm in PVC insulated 1100V grade multistrand single core copper conductor cable in 20 mm dia heavy duty (2mm thick)PVC conduit concealed in wall, complete with one number 2.5 sqmm. copper cable as earth continuity wire etc. complet in all respect (PSI No. 216 ( C ) | Rm | 200 | 155 | 31000
60 | Supply and wiring of submain with two number 6 sq.mm in PVC insulated 1100V grade multistrand single core copper conductor cable in 25 mm dia heavy duty (2mm thick)PVC conduit concealed in wall, complete with one number 4.00 sqmm. copper cable as earth continuity wire etc. complet in all respect (PSI No. 217( C ) | Rm | 50 | 215 | 10750
61 | supply and wiring of submain with two number 2.5 sq.mm. FR PVC insulated 1100 V grade multistrand single core copper conductor cable in 20mm dia heavy duty (2mm thick) PVC conduit with 1 number 1.5 sq.mm. FR PVCearth continuity wire complete in all respect including matching colour wash etc. complete in all respect.(PSI No. 1304C) | Rm | 200 | 121 | 24200
62 | supply and wiring of submain with two number 1.5 sq.mm. FR PVC insulated 1100 V grade multistrand single core copper conductor cable in 20mm dia heavy duty (2mm thick) PVC conduit with one number 1.5 sq.mm. FR PVC earth continuity wire complete in all respect including matching colour wash etc. complete in all respect .(PSI No. 1312C) | Rm | 50 | 104 | 5200
63 | S/F of 16 gauge M.S. drum duly painted included making hole in the wall for exhaust fan and finishing proporely complete in all respcet.(PSI No. 1122) | No. | 4 | 680 | 2720
64 | Making hole in the wall for exhaust fan and finishing properly complete in all respect (PSI N0.1121) | No. | 1 | 325 | 325
65 | Supply and fixing of factor fabricated M.S. box in existing sunk of size 600mmx480mmx200mm deep with Godrej type almirah, cover with handle etc. fabricated from 18 SWG ( 1.25mm) M.S. sheet duly painted with red oxide primer followed by two coats of synthetic enamet paint complete with necessary conduit entry and D.P. /T.P.N; fixing arrangement and provision for compartment for loose wires openable housing on the top and hold fast etc. including supply of all material., labour T&P etc. required for proper completion of the work.(PSI No. 1147) | No. | 1 | 1435 | 1435
66 | Supply and fixing of 12inch high speed exhaust fan make-USHA, havels etc or its equivalent including, labour, materials and T&P complete in all respect as directed by E/I. (NSI) | No | 3 | 1686 | 5058
67 | S/F of switch box made up to 16SWG (1.5mm) thick M.S. sheet of 100x100x65mm size duly painted with red oxide primer and flushed in wall ineluding cutting of brick work, fixing it to the level with cement sand mortar, including matching colour wash with s/o all materials, labour and T&P required for proper completion of work as directed a site by the E/I.(PSI No. 159) | No | 2 | 60 | 120
68 | Same as item no 67.but of 150x150x65mm size (PSI No.160) | No | 2 | 95 | 190
69 | Same as item no 67 .but of 175x250x65mm size (PSI No.161) | No | 2 | 90 | 180
70 | Same as item no.67 .but of 200x250x65mm size (PSI No.162) | No | 2 | 145 | 290
71 | Same as item no.67 .but of 250x250x65mm size (PSI No.163) | No | 2 | 165 | 330
72 | Construction of recess of 600mmx480mmx200mm size of main boards, distribution boards of all sizes including cutting of brick work, providing lintel of suitable size and thickness, plastering etc. with supply of all materials, labour T&P required for proper completion of work.(PSI No.1141B) | No. | 1 | 480 | 480
| Total |  |  |  | 844544.3346
| Jr. Engr. | S.D.O |  | Ex. Engineer

## BHIMAPAR
APPROXIMATE BILL OF QUANTITY FOR M&R OF MISC. CIVIL WORKS
AT 33/ 11 K.V. BHIMAPAR, GHAZIPUR
Sl. | ITEM OF WORKS | UNIT | QUANTITY | RATE | AMOUNT
1 | 2 | 3 | 4 | 5 | 6
1 | Dismantiling of existing damaged Mud Faska over the roof. Cleaning the surface with wire brush, removal and disposal of rubbish at a distance 100 meters also including the cost of celaning and stacking of usable materials etc. including all labour, material required for porper completion of work.(CSI No. 15.14) | Sqm | 82.57 | 107 | 8834.99
2 | Dismantling brick work or stone work in lime or cement mortar and including stacking of materials as directied by the E/I. within a distance of 60 metres. (CSI.No.15.01) | Cum. | 2.6 | 389 | 1011.4
3 | Providing of Dr. fixit 301 pidicrete URP & mixing it properly with cement in the proportion of 1:1.5 apply two coat to the prepared surface including cost of labour, material T&P etc. as required for proper completion of work as directed by E/I.(NSI) | Sqm | 82.57 | 262 | 21633.34
4 | R.C.C. work with cement, approved coarse sand and 2 cm. (3/4") gauge approved stone ballast in the proportion of 1:1.5:3 in the SLABS excluding reinforcement and its bending but including its fixing and binding the same with 24 BWG, G.I. binding wire and including necessary centering and shuttering etc. and also including supply of all materials, labour and T&P etc. required for proper completion of the work. (Binding wire to be supplied by the contractor free of cost).(C.S.I. No. 5.24) | Cum. | 7.6 | 9117 | 69289.2
5 | Mild steel of or iron in plain work such as reinforced concrete or reinforced brick work. (when not included in over all rates) wrought to required shape as necessary including bending for proper completion of the work and including supply of steel, its wastage, bend hooks, and authorized overlapping shall be measured. Rainforcement steel of tensile strength 415 N/MM² steel, TMT steel rods of TATA/ SAIL/KAMDHENU or its equivalent (C.S.I. No. 9.03 ) | Qtl. | 3.42 | 6545.2 | 22384.584
6 | Providing and fixing of Dr. fixit LW+ in RCC/CC/PLASTER etc. 200ml per bag of cement as directed by E/I including supply of all material, labour and T&P etc. required for proper completion of work.(NSI) | Ltr | 26.24 | 128.5 | 3371.84
7 | 12mm thick plaster with cement mortar consisting of one par of cement and three part of coarse sand (1:3) minimum thickness not to be less then 10mm including supply of all material, labour and T&P etc. for proper completion of work. (CSI No. 11.06) | Sqm | 250.75 | 175 | 43881.25
8 | 3 mm thick floating coat of neat cement finish including supply of all material, labour and T&P etc. required for proper completion of the work. (Cement consumtion 0.044bag/Sqm.) (CSI No. 11.20+0.044x11.15) | Sqm. | 82.57 | 23.07 | 1904.8899
9 | 1st Class brick ( class-150) work in 1:6 cement and coarse sand (F.M. 1.8.to 2.5 ). mortar in super structure including supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.6.01+6.07+6.08) | Cum. | 2.6 | 5763 | 14983.8
10 | Providing and fixing of 110 mm dia PVC Pipe 6 kg/sq.cm for with special such as Tee, bend, socket, elbow etc including supply of all labour , material T&P etc. complete required for proper completion of the work. (CSI No. 26.17) | Rm | 22.23 | 249 | 5535.27
11 | Dismantiling existing plaster including disposal of refuse as directed by the E/C with in a distance of 60M.(C.S.I.No.15.11) | Sqm | 440.8 | 32 | 14105.6
12 | 12mm thick plaster with cement mortar consisting of one par of cement and four part of coarse sand (1: 4) minimum thickness not to be less then 10mm including supply of all material, labour and T&P etc. for proper completion of work. (CSI No. 11.07) | Sqm | 219.58 | 158 | 34693.64
13 | 12 mm (1/2") thick plaster with cement mortar consisting of one part of cement and 6 part of coarse sand (1:6), minium thickness not to be less then 10mm including suply of all materials, labour and T&P etc. for proper completion of the work.(CSI.NO.11.09) | Sqm. | 183.95 | 148 | 27224.6
14 | Painting two coat with Acrylic/synthetic distemper of Berger/Asian over new wall interior surface over one priming coat cement primer (water based) of ICI or equivalent make as approved by E/I including supply of all materials, labour & T&P etc. required .(C.S.I.No. 13.25+13.26) | Sqm. | 183.95 | 106 | 19498.7
15 | White washing three coat including cost of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.14.03) | Sqm. | 70.18 | 14 | 982.52
16 | Finishing of walls with water proof exterior emulsion paint of ACE of Asian paints or equialent make including 3 coats of above paint including one priming coat on already well prepared new wall surface to give an even shade including cost of all materials, labour and T&P egc. complete for proper completion of the work.(NSI) | Sqm. | 219.58 | 80 | 17566.4
17 | Dismantiling cement concrete or brick or grnolithic floors including base concrete and including stacking of dismantled materials as directed by the E/I. with in a distance 60M.(C.s.I.No.15.05) | Sqm | 270.59 | 44 | 11905.96
18 | Clearing of septic tank including disposal of waste out side the UPPCL area as per direction of the E/I. including cost of all labour T&P etc. required for proper completion of the work.(CSI No. 20.12) | N0 | 1 | 1348 | 1348
19 | 40 mm. thick C.C. 1:2:4 plain cement concrete floor with cement, approved coarse sand, and 2cm.(3/4") graded approved stone ballast laid in pannels finished with 3mm.(1/8") floating coat of neat cement or cement and marble dust in ratio of 5:1 as specified over and removing any over lapping mortar at the joints of the pannels, if any, and giving them a uniform finish including supply of all materials labour and T&P etc. required for proper completion of the work with without base concrete.(C.S.I.No.12.04) | Sqm. | 230.62 | 375 | 86482.5
20 | Providing and fixing glass strips of 3.15 mm thickness & 40mm depth in joints of floor and skriting at the time of laying floors, flush with floor level including supply of labour T&P etc. required for proper completion of the work. (C.S.I. No. 12.14) | Rm | 116 | 28 | 3248
21 | 1st Class brick ( class-150) work in 1:6 cement and coarse sand (F.M. 1.5.to 2.0 ). mortar in foundation and plinth including supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.6.01) | Cum. | 15.45 | 5205 | 80417.25
22 | Concrete with 4cm gauge stone ballast coarse sand ( F.M. 1.8 to 2.5) & cement in proportion of 12:6:1 in foundation & under floors including supply of all materials, labour and T&P etc. required for proper completion of work.(CSI No. 5.02) | Cum. | 30.6 | 4167 | 127510.2
23 | Local river sand filling in plinth including supply of necessary quantity of sand from a distances not exceeding 8 Kms. (5 miles) from the site of work including watering ramming and dressing etc. Rate include cost of all materials, labour and T & P etc. required for proper completion of the work.(C.S.I. No. 4.05) | Cum. | 15.98 | 587 | 9380.26
24 | Supply and Laying 8 mm thick glazed floor tiles of Somany, Johnson or equivalent make, of size 300x300 mm, laid with 1:3 cement and approved coarse sand mortar finished with white cement slurry, jointing and polishing complete, including supply of all materials, labour and T&P etc. completion required for proper completion of the work. (CSI No. 12.11) | Sqm | 3.9 | 1165 | 4543.5
25 | Supply and Laying 6 mm thick glazed tiles of size 200x300 mm in skirting / dado laid with 1:3 cement and approved coarse sand mortar finished with white cement slurry, jointing and polishing complete,including supply of all materials, labour and T&P etc. completion required for proper completion of the work. (CSI No. 12.12) | Sqm | 12.76 | 1000 | 12760
26 | Providing and fixing white glazed China earthen ware water closet squatting " Orisa type" pan weaper size 580mmx140mm Hindustan Make or other equivalent approved make of Ist quality with 100mm dia. White glazed P or S trap fittings including cutting & making good the walls and floors wherever required with cement sand and grit mortar not less than 1:4 the seat and trap shall have to be fixed over minimum 3" thick c.c. in proportion of 12:6:1 including cost of all materials, labour(C.S.I.No. 27.01+27.23) | Nos. | 1 | 2891 | 2891
27 | Dismantling of doors or window chowkhats including stacking of materials as directed by the E/I. within a distance of 60M.(CSI No. 15.10) | Sqm | 19.62 | 57 | 1118.34
28 | Supply and fixing of 32 mm thick single leaf flush door shutter (boiled water resistaance, phenol maldehide resin bonded, hot pressed factory made ( commercial quality to I.S. 2202 part-1 (1993) ISI marked including fixing of wooden leats and stoppers and including fixing and adjustment of hinges bolts, lokcs, handles, springs and other fitting but excluding their supply including all materials, labour & T&P etc. required for proper completion of work. ( CSI No. 8.57) | Sqm. | 6.52 | 1559 | 10164.68
29 | Mild steel or iron work in heavy sizes such as trusses built-up gates, door frames, record, racks, roof work, gates etc. wrought to required form including holes rivetting or welding where necessary and also fixing in proper position and alignment including cost of all materials supplied by contractor (CSI No. 9.01 ) | Qtl. | 11 | 7491.9 | 82410.9
30 | Supply and fixing galvanised mosquito proof jali ( 16x24 gauge ) with M.S. flat of 20x3mm. Size on both sides screwed or welded to window or door frame.(CSI No. 9.18) | Sqm | 9.63 | 582 | 5604.66
31 | Providing and fixing steel glazed window and ventilators of standard rolled Mann or mahavir steel section conforming to IS 7452-1974 as per drawing joints metered & welded with 100x14x3.15mm holdfast embedded in cement conctete block 15x10x10 cm. size of 1:3:6 proportion I.E. First part of cement 3 part of approved coarse sand & 6 part of graded stone (aggregated 20mm. Nominal size) S/F of glass panes of plain pin headed 4mm. Thick nuts glazing clips and special putty of approved make complete and including a cost of red oxide paint. The fabrication should conform to I.S. 1038-1975 ( Aluminum beading with rubber packing included) (CSI No. 9.17) | Sqm | 9.63 | 3828 | 36863.64
32 | Painting or varnishing new iron works or new wood work with one coat of ready mixed priming paint and two coats of approved superior quality ready mixed enamel paint 'LUXOL' or equivalent brand or varnish including supply of all materials, labour& T&P etc. required for proper completion of the work (C.S.I. No. 13.01+13.02) | Sqm. | 38.93 | 97 | 3776.21
33 | Pre-Construction anti-termite treatment, by breating a barrier under and around the coloumns pits, foundation trenches, under floors, junctions of walls & floors, around the external perimetre of building, expansion, joints, surrounding of pipes and coduits etc.(Plinth area of the building at ground floor only shall be measured as per I.S. 6313 ( Part II 1981 ) with Aldine exulsifiable 0.2% concentration or any other approved material such as Heptachlore or chlordance will be used. The consumption of emulsion shall be (i) Foundation and masonary @ 5 Ltrs /Sqm (ii) Back fills in immediate contact of foundation@ 7.5 Ltrs/Sqm ((iii) Top surface of plinth filling @ 5 Ltrs/Sqm,(iv) junction of walls & floors @ 7.5 Ltrs/Sqm (v) Soil along extermal perlimetre of building @ 7.5 Ltrs/Sqm(vi) under apron of the building @ 5 Ltrs/Sqm. The rates includes cost of all materials, labour, equipments, T&P complete.(CSI No. 17.01) | Sqm | 73.38 | 82 | 6017.16
34 | Concrete with 20mm. (1.5") gauge approved hard Stone ballast, coarse sand of ( F.M.1.5 to 2.0) and cement in proportion of 4:2:1in foundation and under floors and supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. NO. 5.06) | Cum. | 0.57 | 6386 | 3640.02
35 | Clearing jungle including uprooting of rank vegetations grass, bush, wood, trees and saplings of girth up to 30cm measured at a height of 1.0m above ground level and removal of rubbish up to a distance of 50m outside the periphery of UPPCL area cleared.(CSI No. 4.08) | Sqm | 150 | 5 | 750
36 | Providing and Fixing barbed iron wire wire fencing including stretching, fixing in to the post including all labour, materials and T&P required for proper completion of work the weight of hot dipped GI barbed wire having 12 SWG-2 ply wires and 4 point ordinary barbs @ 150mm (approx ) C/C should be 100 gm per Meter.(CSI No. 9.07) | Rmt. | 90 | 11 | 990
37 | Excavation in foundation in ordinary soil (Loam Clay or Sand) including lift upto 1.5 meter and lead upto 30 meter and including filling , watering, and ramming of excavated earth into the trenches or into the space between the building and sides of the foundation the work . (C.S.I. No 4.01) | Cum. | 7.2 | 133 | 957.6
38 | Disposal of rubbish/debris out side the UPPCL area as per direction of E/I. including cartage, labour and materials, T&P etc. required for proper completion of the work. ( No deduction for voids shall be made ) ( CSI No. 20.16). | Cum. | 15.4 | 264 | 4065.6
39 | First class brick ( Class-150) laid dry in foundation and plinth as in circular sockpit walls of one brick thickness and 2.0 to 3.0M depth including cutting moulding bricks as required including cost of all materials, labour and T&P complete (CSI No. 6.16) | Cum. | 0.8 | 4749 | 3799.2
40 | Providing and laying floor of 10mm thick industrial (heavy duty) tiles in flooring or skirting of approved brand ( Bell, Johnson or equil, make) size of 300x300mm of approved shade, clour and pattern, laid over base cement mortar 1:4 mix icluding finishing the joints with white cement mixed with pigment to match the shade of tile including cost of all material, labour and T&P required for proper completion of the work.( NSI) | Sqm | 50 | 1728 | 86400
41 | Add for extra labour and materials for plaster over rough face of one brick thick wall.(CSI No. 11.12) | Sqm | 220 | 20 | 4400
42 | Firs class bricks on edge floor laid dry joints sand filed including preparation of base to proper slope and its ramming including supply of all material labour & T&P etc. required for proper completion of the work.(CSI No. 12.07) | Sqm | 40 | 558 | 22320
43 | Providing and fixing 1mm thick M.S. sheet garrage door with frame of 40x40x6mm angle iron, diagonal bracings with 50x5 mm flat and 5mm thick M.S.gusset plates at the junctions and corner including supply and fixing of necessary fitting 2 no. lock rail of 16 dia , 375mm long and including pintel hooks at the top and bottom, applying a priming coat of red oxide paint on all sides complete. (CSI No.9.34) | Sqm | 1.24 | 3002 | 3722.48
44 | Removal of cement mortar from dismenttled bricks and stacking in countable position at place as directed by the E/I. including cost of all labour and T&P required for proper completion of work. (CSI No. 6.22) | Cum. | 6.64 | 989 | 6566.96
46 | Wiring point for light with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch & ceiling rose /single/batten holder on 3mm. thick phenolic laminated backelite sheet etc. complete in all respect, as directed including matching colour wash (PSI N0 131(C ) | Nos. | 10 | 518 | 5180
47 | Wiring point for fan /fresh air fan with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch & ceiling rose on 3mm. thick phenolic laminated backelite sheet etc. complete in all respect, as directed including matching colour wash(PSI N0.133( C) | NO | 4 | 595 | 2380
48 | Wiring point for plug with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch and socket etc.complete in all respect, including matching colour wash((PSI N0.134(C ) | NO | 5 | 275 | 1375
49 | Wiring point for exhaust fan with 1.5sq.mm FR PVC insulated multistrand single core copper conductor cable in PVCl conduit concealed in the wall, complete with 14 SWG copper earth continuity wire and 15 A piano type ceiling rose on 3mm thick phenolic laminated backelite sheet etc. complete in all respect including matching colour wash (PSI No. 137 (C ) | No. | 3 | 780 | 2340
50 | S/F of LED fluorescent tube light fitting suitable for 1x18 watt fluorescent tube complete including tubes etc. on surface complete in all respects.(NSI) | Each | 10 | 1100 | 11000
51 | Supply and fixing of high speed ceiling fan 1200mm size of USHA or any approved make by E/I. complet in all respect (NSI) | No. | 4 | 1686 | 6744
52 | S/F of MCB ( 6-32Amp) PSI 1002 CAT-A | No | 8 | 250 | 2000
53 | S&F surface/flush mounting 12 ways SPN distribution board ( Legrand Lexic ) with additional metal door without MCB complete in all respect, as directed at site by E/I (PSI N0.1025A) | No | 1 | 2100 | 2100
54 | S/F of electronic fan dimmer, 120-280V , ISI marked on the existing switch board including making connnection, required material, labour T&P egc. For proper completion of work to the satisfaction of E/I. of work (PSI 1203(A) | No. | 4 | 305 | 1220
55 | Supply and fixing of power plug with 20A/250 volt flush type switch and 5 pin 20A/250V flush type universal socket in suitable M.S. box of 175mmx100mmx50mm size with phenoic laminated bakelite sheet cover 3mm thick fixed with brass machinne screw and cup washer (PSI N0.1139) (A) | No. | 4 | 595 | 2380
56 | S& F of Electrical (Porcelain) Cut Out 63Amp as directed by E/I(NSI) | No. | 4 | 300 | 1200
57 | supply and burying of 600mmx600mmx6mm GI plate vertically for earthing with its top at least 3 metres below ground tevel complete with 20mm dia g.I. pipe and funned for watering and one eahing lead of one no. 8 to 10 SWG copper wire in 15mm dia G.I.pipe up to switch board (From appron to switch board the cost of G.I. pipe and G.I. wire will be extra) 30cm square C.I. frame with hinged cover masonry housing alternate layers of charcoal/coke and salt at least 150mm thick alround etc. as per direction of E/I. complete in all respect\ (PSI N0 703) | No. | 1 | 4730 | 4730
58 | 63Amp.Double Pole Isolator (Legrand Lexic) (PSI N0 1005B) | No | 1 | 590 | 590
59 | S&F hexagonal fan box with hexagonal side of approx 80mm in length fabricated from 16 SWG MS sheet incorporating 10mm dia M.S. round bar duly bent for supporting fan hanger duly painted withred oxide and screwing arrangement with wiring conduit laid in the RCC roof before concreting along with supply of all material, labour and T&P etc. required for proper completion of the work (PSI No. 1149) | No. | 4 | 135 | 540
60 | Supply and wiring of submain with two number 4 sq.mm in PVC insulated 1100V grade multistrand single core copper conductor cable in 20 mm dia heavy duty (2mm thick)PVC conduit concealed in wall, complete with one number 2.5 sqmm. copper cable as earth continuity wire etc. complet in all respect (PSI No. 216 ( C ) | Rm | 200 | 155 | 31000
61 | Supply and wiring of submain with two number 6 sq.mm in PVC insulated 1100V grade multistrand single core copper conductor cable in 25 mm dia heavy duty (2mm thick)PVC conduit concealed in wall, complete with one number 4.00 sqmm. copper cable as earth continuity wire etc. complet in all respect (PSI No. 217( C ) | Rm | 50 | 215 | 10750
62 | supply and wiring of submain with two number 2.5 sq.mm. FR PVC insulated 1100 V grade multistrand single core copper conductor cable in 20mm dia heavy duty (2mm thick) PVC conduit with 1 number 1.5 sq.mm. FR PVCearth continuity wire complete in all respect including matching colour wash etc. complete in all respect.(PSI No. 1304C) | Rm | 200 | 121 | 24200
63 | supply and wiring of submain with two number 1.5 sq.mm. FR PVC insulated 1100 V grade multistrand single core copper conductor cable in 20mm dia heavy duty (2mm thick) PVC conduit with one number 1.5 sq.mm. FR PVC earth continuity wire complete in all respect including matching colour wash etc. complete in all respect .(PSI No. 1312C) | Rm | 50 | 104 | 5200
64 | S/F of 16 gauge M.S. drum duly painted included making hole in the wall for exhaust fan and finishing proporely complete in all respcet.(PSI No. 1122) | No. | 4 | 680 | 2720
65 | Making hole in the wall for exhaust fan and finishing properly complete in all respect (PSI N0.1121) | No. | 1 | 325 | 325
66 | Supply and fixing of factor fabricated M.S. box in existing sunk of size 600mmx480mmx200mm deep with Godrej type almirah, cover with handle etc. fabricated from 18 SWG ( 1.25mm) M.S. sheet duly painted with red oxide primer followed by two coats of synthetic enamet paint complete with necessary conduit entry and D.P. /T.P.N; fixing arrangement and provision for compartment for loose wires openable housing on the top and hold fast etc. including supply of all material., labour T&P etc. required for proper completion of the work.(PSI No. 1147) | No. | 1 | 1435 | 1435
67 | Supply and fixing of 12inch high speed exhaust fan make-USHA, havels etc or its equivalent including, labour, materials and T&P complete in all respect as directed by E/I. (NSI) | No | 3 | 1686 | 5058
68 | S/F of switch box made up to 16SWG (1.5mm) thick M.S. sheet of 100x100x65mm size duly painted with red oxide primer and flushed in wall ineluding cutting of brick work, fixing it to the level with cement sand mortar, including matching colour wash with s/o all materials, labour and T&P required for proper completion of work as directed a site by the E/I.(PSI No. 159) | No | 2 | 60 | 120
69 | Same as item no 68.but of 150x150x65mm size (PSI No.160) | No | 2 | 95 | 190
70 | Same as item no 68 .but of 175x250x65mm size (PSI No.161) | No | 2 | 90 | 180
71 | Same as item no.68 .but of 200x250x65mm size (PSI No.162) | No | 2 | 145 | 290
72 | Same as item no.68 .but of 250x250x65mm size (PSI No.163) | No | 2 | 165 | 330
73 | Earth filling under floors and in substation area including cost of earth. Earth to be obtained from outside the Corporation's area including its cartage and ramming, watering, dressing in 20 cm. thick layers and dressing of earth etc. complete including cost of earth with all lead and lift etc. complete.(C.S.I. No.4.10) | Cum | 35.52 | 349 | 12396.48
74 | Providing and fixing 1mm thick M.S. sheet garrage door with frame of 40x40x6mm angle iron, diagonal bracings with 50x5 mm flat and 5mm thick M.S.gusset plates at the junctions and corner including supply and fixing of necessary fitting 2 no. lock rail of 16 dia , 375mm long and including pintel hooks at the top and bottom, applying a priming coat of red oxide paint on all sides complete. (CSI No.9.34) | Sqm | 1.24 | 3002 | 3722.48
75 | Providing and laying floor of 10mm thick industrial (heavy duty) tiles in flooring or skirting of approved brand ( Bell, Johnson or equil, make) size of 300x300mm of approved shade, clour and pattern, laid over base cement mortar 1:4 mix icluding finishing the joints with white cement mixed with pigment to match the shade of tile including cost of all material, labour and T&P required for proper completion of the work.( NSI) | Sqm | 47.77 | 1728 | 82546.56
76 | Add for extra labour and materials for plaster over rough face of one brick thick wall.(CSI No. 11.12) | Sqm | 220 | 20 | 4400
77 | Construction of recess of 600mmx480mmx200mm size of main boards, distribution boards of all sizes including cutting of brick work, providing lintel of suitable size and thickness, plastering etc. with supply of all materials, labour T&P required for proper completion of work.(PSI No.1141B) | No. | 1 | 480 | 480
| Total |  |  |  | 1160078.6639
| Jr. Engr. | S.D.O |  | Ex. Engineer

## SADAT
APPROXIMATE BILL OF QUANTITY FOR M&R OF MISC. CIVIL WORKS
AT 33/ 11 K.V. SADAT, GHAZIPUR
Sl. | ITEM OF WORKS | UNIT | QUANTITY | RATE | AMOUNT
1 | 2 | 3 | 4 | 5 | 6
1 | Dismantiling of existing damaged Mud Faska over the roof. Cleaning the surface with wire brush, removal and disposal of rubbish at a distance 100 meters also including the cost of celaning and stacking of usable materials etc. including all labour, material required for porper completion of work.(CSI No. 15.14) | Sqm | 102.64 | 107 | 10982.48
2 | Dismantling brick work or stone work in lime or cement mortar and including stacking of materials as directied by the E/I. within a distance of 60 metres. (CSI.No.15.01) | Cum. | 2.27 | 389 | 883.03
3 | Providing of Dr. fixit 301 pidicrete URP & mixing it properly with cement in the proportion of 1:1.5 apply two coat to the prepared surface including cost of labour, material T&P etc. as required for proper completion of work as directed by E/I.(NSI) | Sqm | 102.64 | 262 | 26891.68
4 | R.C.C. work with cement, approved coarse sand and 2 cm. (3/4") gauge approved stone ballast in the proportion of 1:1.5:3 in the SLABS excluding reinforcement and its bending but including its fixing and binding the same with 24 BWG, G.I. binding wire and including necessary centering and shuttering etc. and also including supply of all materials, labour and T&P etc. required for proper completion of the work. (Binding wire to be supplied by the contractor free of cost).(C.S.I. No. 5.24) | Cum. | 6.5 | 9117 | 59260.5
5 | Mild steel of or iron in plain work such as reinforced concrete or reinforced brick work. (when not included in over all rates) wrought to required shape as necessary including bending for proper completion of the work and including supply of steel, its wastage, bend hooks, and authorized overlapping shall be measured. Rainforcement steel of tensile strength 415 N/MM² steel, TMT steel rods of TATA/ SAIL/KAMDHENU or its equivalent (C.S.I. No. 9.03 ) | Qtl. | 4.65 | 6545.2 | 30435.18
6 | Providing and fixing of Dr. fixit LW+ in RCC/CC/PLASTER etc. 200ml per bag of cement as directed by E/I including supply of all material, labour and T&P etc. required for proper completion of work.(NSI) | Ltr | 23 | 128.5 | 2955.5
7 | 12mm thick plaster with cement mortar consisting of one par of cement and three part of coarse sand (1:3) minimum thickness not to be less then 10mm including supply of all material, labour and T&P etc. for proper completion of work. (CSI No. 11.06) | Sqm | 190 | 175 | 33250
8 | 3 mm thick floating coat of neat cement finish including supply of all material, labour and T&P etc. required for proper completion of the work. (Cement consumtion 0.044bag/Sqm.) (CSI No. 11.20+0.044x11.15) | Sqm. | 102.64 | 23.07 | 2367.9048
9 | 1st Class brick ( class-150) work in 1:6 cement and coarse sand (F.M. 1.8.to 2.5 ). mortar in super structure including supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.6.01+6.07+6.08) | Cum. | 2.27 | 5763 | 13082.01
10 | Providing and fixing of 110 mm dia PVC Pipe 6 kg/sq.cm for with special such as Tee, bend, socket, elbow etc including supply of all labour , material T&P etc. complete required for proper completion of the work. (CSI No. 26.17) | Rm | 20 | 249 | 4980
11 | Dismantiling existing plaster including disposal of refuse as directed by the E/C with in a distance of 60M.(C.S.I.No.15.11) | Sqm | 410.56 | 32 | 13137.92
12 | 12mm thick plaster with cement mortar consisting of one par of cement and four part of coarse sand (1: 4) minimum thickness not to be less then 10mm including supply of all material, labour and T&P etc. for proper completion of work. (CSI No. 11.07) | Sqm | 220.45 | 158 | 34831.1
13 | 12 mm (1/2") thick plaster with cement mortar consisting of one part of cement and 6 part of coarse sand (1:6), minium thickness not to be less then 10mm including suply of all materials, labour and T&P etc. for proper completion of the work.(CSI.NO.11.09) | Sqm. | 195.85 | 148 | 28985.8
14 | Painting two coat with Acrylic/synthetic distemper of Berger/Asian over new wall interior surface over one priming coat cement primer (water based) of ICI or equivalent make as approved by E/I including supply of all materials, labour & T&P etc. required .(C.S.I.No. 13.25+13.26) | Sqm. | 220.45 | 106 | 23367.7
15 | White washing three coat including cost of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.14.03) | Sqm. | 90.23 | 14 | 1263.22
16 | Finishing of walls with water proof exterior emulsion paint of ACE of Asian paints or equialent make including 3 coats of above paint including one priming coat on already well prepared new wall surface to give an even shade including cost of all materials, labour and T&P egc. complete for proper completion of the work.(NSI) | Sqm. | 195.85 | 80 | 15668
17 | Dismantiling cement concrete or brick or grnolithic floors including base concrete and including stacking of dismantled materials as directed by the E/I. with in a distance 60M.(C.s.I.No.15.05) | Sqm | 200.45 | 44 | 8819.8
19 | 40 mm. thick C.C. 1:2:4 plain cement concrete floor with cement, approved coarse sand, and 2cm.(3/4") graded approved stone ballast laid in pannels finished with 3mm.(1/8") floating coat of neat cement or cement and marble dust in ratio of 5:1 as specified over and removing any over lapping mortar at the joints of the pannels, if any, and giving them a uniform finish including supply of all materials labour and T&P etc. required for proper completion of the work with without base concrete.(C.S.I.No.12.04) | Sqm. | 200.45 | 375 | 75168.75
20 | Providing and fixing glass strips of 3.15 mm thickness & 40mm depth in joints of floor and skriting at the time of laying floors, flush with floor level including supply of labour T&P etc. required for proper completion of the work. (C.S.I. No. 12.14) | Rm | 75 | 28 | 2100
21 | 1st Class brick ( class-150) work in 1:6 cement and coarse sand (F.M. 1.5.to 2.0 ). mortar in foundation and plinth including supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. No.6.01) | Cum. | 14.3 | 5205 | 74431.5
22 | Concrete with 4cm gauge stone ballast coarse sand ( F.M. 1.8 to 2.5) & cement in proportion of 12:6:1 in foundation & under floors including supply of all materials, labour and T&P etc. required for proper completion of work.(CSI No. 5.02) | Cum. | 10.25 | 4167 | 42711.75
23 | Local river sand filling in plinth including supply of necessary quantity of sand from a distances not exceeding 8 Kms. (5 miles) from the site of work including watering ramming and dressing etc. Rate include cost of all materials, labour and T & P etc. required for proper completion of the work.(C.S.I. No. 4.05) | Cum. | 36.62 | 587 | 21495.94
27 | Dismantling of doors or window chowkhats including stacking of materials as directed by the E/I. within a distance of 60M.(CSI No. 15.10) | Sqm | 15.52 | 57 | 884.64
28 | Supply and fixing of 32 mm thick single leaf flush door shutter (boiled water resistaance, phenol maldehide resin bonded, hot pressed factory made ( commercial quality to I.S. 2202 part-1 (1993) ISI marked including fixing of wooden leats and stoppers and including fixing and adjustment of hinges bolts, lokcs, handles, springs and other fitting but excluding their supply including all materials, labour & T&P etc. required for proper completion of work. ( CSI No. 8.57) | Sqm. | 6.62 | 1559 | 10320.58
29 | Mild steel or iron work in heavy sizes such as trusses built-up gates, door frames, record, racks, roof work, gates etc. wrought to required form including holes rivetting or welding where necessary and also fixing in proper position and alignment including cost of all materials supplied by contractor (CSI No. 9.01 ) | Qtl. | 14.5 | 7491.9 | 108632.55
30 | Supply and fixing galvanised mosquito proof jali ( 16x24 gauge ) with M.S. flat of 20x3mm. Size on both sides screwed or welded to window or door frame.(CSI No. 9.18) | Sqm | 4.68 | 582 | 2723.76
31 | Providing and fixing steel glazed window and ventilators of standard rolled Mann or mahavir steel section conforming to IS 7452-1974 as per drawing joints metered & welded with 100x14x3.15mm holdfast embedded in cement conctete block 15x10x10 cm. size of 1:3:6 proportion I.E. First part of cement 3 part of approved coarse sand & 6 part of graded stone (aggregated 20mm. Nominal size) S/F of glass panes of plain pin headed 4mm. Thick nuts glazing clips and special putty of approved make complete and including a cost of red oxide paint. The fabrication should conform to I.S. 1038-1975 ( Aluminum beading with rubber packing included) (CSI No. 9.17) | Sqm | 6.68 | 3828 | 25571.04
32 | Painting or varnishing new iron works or new wood work with one coat of ready mixed priming paint and two coats of approved superior quality ready mixed enamel paint 'LUXOL' or equivalent brand or varnish including supply of all materials, labour& T&P etc. required for proper completion of the work (C.S.I. No. 13.01+13.02) | Sqm. | 37.14 | 97 | 3602.58
33 | Pre-Construction anti-termite treatment, by breating a barrier under and around the coloumns pits, foundation trenches, under floors, junctions of walls & floors, around the external perimetre of building, expansion, joints, surrounding of pipes and coduits etc.(Plinth area of the building at ground floor only shall be measured as per I.S. 6313 ( Part II 1981 ) with Aldine exulsifiable 0.2% concentration or any other approved material such as Heptachlore or chlordance will be used. The consumption of emulsion shall be (i) Foundation and masonary @ 5 Ltrs /Sqm (ii) Back fills in immediate contact of foundation@ 7.5 Ltrs/Sqm ((iii) Top surface of plinth filling @ 5 Ltrs/Sqm,(iv) junction of walls & floors @ 7.5 Ltrs/Sqm (v) Soil along extermal perlimetre of building @ 7.5 Ltrs/Sqm(vi) under apron of the building @ 5 Ltrs/Sqm. The rates includes cost of all materials, labour, equipments, T&P complete.(CSI No. 17.01) | Sqm | 95 | 82 | 7790
34 | Concrete with 20mm. (1.5") gauge approved hard Stone ballast, coarse sand of ( F.M.1.5 to 2.0) and cement in proportion of 4:2:1in foundation and under floors and supply of all materials, labour and T&P etc. required for proper completion of the work. (C.S.I. NO. 5.06) | Cum. | 0.57 | 6386 | 3640.02
35 | Clearing jungle including uprooting of rank vegetations grass, bush, wood, trees and saplings of girth up to 30cm measured at a height of 1.0m above ground level and removal of rubbish up to a distance of 50m outside the periphery of UPPCL area cleared.(CSI No. 4.08) | Sqm | 150 | 5 | 750
36 | Providing and Fixing barbed iron wire wire fencing including stretching, fixing in to the post including all labour, materials and T&P required for proper completion of work the weight of hot dipped GI barbed wire having 12 SWG-2 ply wires and 4 point ordinary barbs @ 150mm (approx ) C/C should be 100 gm per Meter.(CSI No. 9.07) | Rmt. | 200 | 11 | 2200
37 | Excavation in foundation in ordinary soil (Loam Clay or Sand) including lift upto 1.5 meter and lead upto 30 meter and including filling , watering, and ramming of excavated earth into the trenches or into the space between the building and sides of the foundation the work . (C.S.I. No 4.01) | Cum. | 7.2 | 133 | 957.6
38 | Disposal of rubbish/debris out side the UPPCL area as per direction of E/I. including cartage, labour and materials, T&P etc. required for proper completion of the work. ( No deduction for voids shall be made ) ( CSI No. 20.16). | Cum. | 15.4 | 264 | 4065.6
39 | First class brick ( Class-150) laid dry in foundation and plinth as in circular sockpit walls of one brick thickness and 2.0 to 3.0M depth including cutting moulding bricks as required including cost of all materials, labour and T&P complete (CSI No. 6.16) | Cum. | 0.8 | 4749 | 3799.2
40 | Providing and laying floor of 10mm thick industrial (heavy duty) tiles in flooring or skirting of approved brand ( Bell, Johnson or equil, make) size of 300x300mm of approved shade, clour and pattern, laid over base cement mortar 1:4 mix icluding finishing the joints with white cement mixed with pigment to match the shade of tile including cost of all material, labour and T&P required for proper completion of the work.( NSI) | Sqm | 25 | 1728 | 43200
41 | Add for extra labour and materials for plaster over rough face of one brick thick wall.(CSI No. 11.12) | Sqm | 220 | 20 | 4400
42 | Firs class bricks on edge floor laid dry joints sand filed including preparation of base to proper slope and its ramming including supply of all material labour & T&P etc. required for proper completion of the work.(CSI No. 12.07) | Sqm | 40 | 558 | 22320
43 | Providing and fixing 1mm thick M.S. sheet garrage door with frame of 40x40x6mm angle iron, diagonal bracings with 50x5 mm flat and 5mm thick M.S.gusset plates at the junctions and corner including supply and fixing of necessary fitting 2 no. lock rail of 16 dia , 375mm long and including pintel hooks at the top and bottom, applying a priming coat of red oxide paint on all sides complete. (CSI No.9.34) | Sqm | 1.24 | 3002 | 3722.48
44 | Removal of cement mortar from dismenttled bricks and stacking in countable position at place as directed by the E/I. including cost of all labour and T&P required for proper completion of work. (CSI No. 6.22) | Cum. | 6.64 | 989 | 6566.96
46 | Wiring point for light with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch & ceiling rose /single/batten holder on 3mm. thick phenolic laminated backelite sheet etc. complete in all respect, as directed including matching colour wash (PSI N0 131(C ) | Nos. | 10 | 518 | 5180
47 | Wiring point for fan /fresh air fan with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch & ceiling rose on 3mm. thick phenolic laminated backelite sheet etc. complete in all respect, as directed including matching colour wash(PSI N0.133( C) | NO | 4 | 595 | 2380
48 | Wiring point for plug with 1.5sq.mm FR PVC insulated multistrand single copper conductor cable in PVC conduit pipe concealed in the wall, complete with 14 SWG copper continuity wire, piano type switch and socket etc.complete in all respect, including matching colour wash((PSI N0.134(C ) | NO | 5 | 275 | 1375
49 | Wiring point for exhaust fan with 1.5sq.mm FR PVC insulated multistrand single core copper conductor cable in PVCl conduit concealed in the wall, complete with 14 SWG copper earth continuity wire and 15 A piano type ceiling rose on 3mm thick phenolic laminated backelite sheet etc. complete in all respect including matching colour wash (PSI No. 137 (C ) | No. | 3 | 780 | 2340
50 | S/F of LED fluorescent tube light fitting suitable for 1x18 watt fluorescent tube complete including tubes etc. on surface complete in all respects.(NSI) | Each | 10 | 1100 | 11000
51 | Supply and fixing of high speed ceiling fan 1200mm size of USHA or any approved make by E/I. complet in all respect (NSI) | No. | 4 | 1686 | 6744
52 | S/F of MCB ( 6-32Amp) PSI 1002 CAT-A | No | 8 | 250 | 2000
53 | S&F surface/flush mounting 12 ways SPN distribution board ( Legrand Lexic ) with additional metal door without MCB complete in all respect, as directed at site by E/I (PSI N0.1025A) | No | 1 | 2100 | 2100
54 | S/F of electronic fan dimmer, 120-280V , ISI marked on the existing switch board including making connnection, required material, labour T&P egc. For proper completion of work to the satisfaction of E/I. of work (PSI 1203(A) | No. | 4 | 305 | 1220
55 | Supply and fixing of power plug with 20A/250 volt flush type switch and 5 pin 20A/250V flush type universal socket in suitable M.S. box of 175mmx100mmx50mm size with phenoic laminated bakelite sheet cover 3mm thick fixed with brass machinne screw and cup washer (PSI N0.1139) (A) | No. | 4 | 595 | 2380
56 | S& F of Electrical (Porcelain) Cut Out 63Amp as directed by E/I(NSI) | No. | 4 | 300 | 1200
57 | supply and burying of 600mmx600mmx6mm GI plate vertically for earthing with its top at least 3 metres below ground tevel complete with 20mm dia g.I. pipe and funned for watering and one eahing lead of one no. 8 to 10 SWG copper wire in 15mm dia G.I.pipe up to switch board (From appron to switch board the cost of G.I. pipe and G.I. wire will be extra) 30cm square C.I. frame with hinged cover masonry housing alternate layers of charcoal/coke and salt at least 150mm thick alround etc. as per direction of E/I. complete in all respect\ (PSI N0 703) | No. | 1 | 4730 | 4730
58 | 63Amp.Double Pole Isolator (Legrand Lexic) (PSI N0 1005B) | No | 1 | 590 | 590
59 | S&F hexagonal fan box with hexagonal side of approx 80mm in length fabricated from 16 SWG MS sheet incorporating 10mm dia M.S. round bar duly bent for supporting fan hanger duly painted withred oxide and screwing arrangement with wiring conduit laid in the RCC roof before concreting along with supply of all material, labour and T&P etc. required for proper completion of the work (PSI No. 1149) | No. | 4 | 135 | 540
60 | Supply and wiring of submain with two number 4 sq.mm in PVC insulated 1100V grade multistrand single core copper conductor cable in 20 mm dia heavy duty (2mm thick)PVC conduit concealed in wall, complete with one number 2.5 sqmm. copper cable as earth continuity wire etc. complet in all respect (PSI No. 216 ( C ) | Rm | 200 | 155 | 31000
61 | Supply and wiring of submain with two number 6 sq.mm in PVC insulated 1100V grade multistrand single core copper conductor cable in 25 mm dia heavy duty (2mm thick)PVC conduit concealed in wall, complete with one number 4.00 sqmm. copper cable as earth continuity wire etc. complet in all respect (PSI No. 217( C ) | Rm | 50 | 215 | 10750
62 | supply and wiring of submain with two number 2.5 sq.mm. FR PVC insulated 1100 V grade multistrand single core copper conductor cable in 20mm dia heavy duty (2mm thick) PVC conduit with 1 number 1.5 sq.mm. FR PVCearth continuity wire complete in all respect including matching colour wash etc. complete in all respect.(PSI No. 1304C) | Rm | 200 | 121 | 24200
63 | supply and wiring of submain with two number 1.5 sq.mm. FR PVC insulated 1100 V grade multistrand single core copper conductor cable in 20mm dia heavy duty (2mm thick) PVC conduit with one number 1.5 sq.mm. FR PVC earth continuity wire complete in all respect including matching colour wash etc. complete in all respect .(PSI No. 1312C) | Rm | 50 | 104 | 5200
64 | S/F of 16 gauge M.S. drum duly painted included making hole in the wall for exhaust fan and finishing proporely complete in all respcet.(PSI No. 1122) | No. | 4 | 680 | 2720
65 | Making hole in the wall for exhaust fan and finishing properly complete in all respect (PSI N0.1121) | No. | 1 | 325 | 325
66 | Supply and fixing of factor fabricated M.S. box in existing sunk of size 600mmx480mmx200mm deep with Godrej type almirah, cover with handle etc. fabricated from 18 SWG ( 1.25mm) M.S. sheet duly painted with red oxide primer followed by two coats of synthetic enamet paint complete with necessary conduit entry and D.P. /T.P.N; fixing arrangement and provision for compartment for loose wires openable housing on the top and hold fast etc. including supply of all material., labour T&P etc. required for proper completion of the work.(PSI No. 1147) | No. | 1 | 1435 | 1435
67 | Supply and fixing of 12inch high speed exhaust fan make-USHA, havels etc or its equivalent including, labour, materials and T&P complete in all respect as directed by E/I. (NSI) | No | 3 | 1686 | 5058
68 | S/F of switch box made up to 16SWG (1.5mm) thick M.S. sheet of 100x100x65mm size duly painted with red oxide primer and flushed in wall ineluding cutting of brick work, fixing it to the level with cement sand mortar, including matching colour wash with s/o all materials, labour and T&P required for proper completion of work as directed a site by the E/I.(PSI No. 159) | No | 2 | 60 | 120
69 | Same as item no 68.but of 150x150x65mm size (PSI No.160) | No | 2 | 95 | 190
70 | Same as item no 68 .but of 175x250x65mm size (PSI No.161) | No | 2 | 90 | 180
71 | Same as item no.68 .but of 200x250x65mm size (PSI No.162) | No | 2 | 145 | 290
72 | Same as item no.68 .but of 250x250x65mm size (PSI No.163) | No | 2 | 165 | 330
73 | Earth filling under floors and in substation area including cost of earth. Earth to be obtained from outside the Corporation's area including its cartage and ramming, watering, dressing in 20 cm. thick layers and dressing of earth etc. complete including cost of earth with all lead and lift etc. complete.(C.S.I. No.4.10) | Cum | 35.52 | 349 | 12396.48
74 | Providing and fixing 1mm thick M.S. sheet garrage door with frame of 40x40x6mm angle iron, diagonal bracings with 50x5 mm flat and 5mm thick M.S.gusset plates at the junctions and corner including supply and fixing of necessary fitting 2 no. lock rail of 16 dia , 375mm long and including pintel hooks at the top and bottom, applying a priming coat of red oxide paint on all sides complete. (CSI No.9.34) | Sqm | 1.24 | 3002 | 3722.48
75 | Providing and laying floor of 10mm thick industrial (heavy duty) tiles in flooring or skirting of approved brand ( Bell, Johnson or equil, make) size of 300x300mm of approved shade, clour and pattern, laid over base cement mortar 1:4 mix icluding finishing the joints with white cement mixed with pigment to match the shade of tile including cost of all material, labour and T&P required for proper completion of the work.( NSI) | Sqm | 47.77 | 1728 | 82546.56
76 | Add for extra labour and materials for plaster over rough face of one brick thick wall.(CSI No. 11.12) | Sqm | 220 | 20 | 4400
77 | Construction of recess of 600mmx480mmx200mm size of main boards, distribution boards of all sizes including cutting of brick work, providing lintel of suitable size and thickness, plastering etc. with supply of all materials, labour T&P required for proper completion of work.(PSI No.1141B) | No. | 1 | 480 | 480
| Total |  |  |  | 1011339.2948
| Jr. Engr. | S.D.O |  | Ex. Engineer