## Tagore Town
OFFICE OF THE
SUPERINTENDING ENGINEER
ELECTRICITY URBAN DISTRIBUTION CIRCLE-II ALLAHABAD
AGAINST SHORT TERM TENDER NO. 129/EUDCA/SE/2016-17
Sl.No. | Name of work | Unit | Qty. | Rate (Rs) | Amount (Rs)
Repairing & maintenance of 250/400/630 KVA T/F plinth & fencing related works are to be carried out in different 33/11 Sub-station under the jurisdiction of EUDD-Tagore Town, Allahabad
1 | Opening of HT & LT connection from existing T/F shifting of 11/.4 KV 630/400/250 KVA T/F from existing damaged plinth to mobile trolley, re-energize the T/F of mobile trolley after making all HT/LT connections. Repairing of existing damaged plinth with cement, sand & brick ballast etc including 1st class brick work as per requirement as per RESSPO Norms. Opening of HT & LT connections of T/F installed at mobile trolly & re-shifting of T/F on repaired plinth & making all HT & LT connection & re-energize the T/F as per instruction of SDO/JE in-charge. | Job | 10
2 | Construction of retaining wall, fabrication and erection of wiremesh fencing 5'. Height with locking arrangement including grouting of fabricated MS Angle 50x50x6 mm, paining of fencing and support with all material as per RESPO norms around 11/0.4 kV substation with D.P. Box of size 2x (5+3x2) Sq.mm.. The fencing shall be made of 50x25 mm 10 SWG rectangular type of wiremesh. Wiremesh shall be fixed on panel made of 40x40x5 mm MS Angle Iron. The wiremesh on panel will be supported by 25x3 mm MS Flat on all the bracings diagonally and 40x5 mm MS Angle iron horizontally at the centre of the panel. The panel will be jointed by bolts and nuts of appropriate size with each other and on the main support of the corner. (All materials will be arranged by the conctractor) | Rmt. | 20
3 | Construction of special type pipe earthing of 11 KV/0.4 33 KV substation by using G.I. Pipe of diameter 1.5 inch. The work involves hand pipe type earth boring up to the second strata of water, minimum 40'. About 6 inch of G.I Pipe shall remain above ground level as per drawing enclosed 1 No. G.I. Earth clamp shall also be welded to the portion of pipe which is above he ground level. Through this G.I. Clamp, a G.I. Strip 30x5 mm duly galvanized shall be connected with nut and bolts. For earthing of Neutral of Distribution Transformer. | Job | 10
Total
SUPERINTENDING ENGINEER |  | SIGNATURE OF TENDERER
E.U.D.C-II, ALLAHABAD |  | ALONG WITH SEAL